**Chapter 3 Wiring Methods and Materials**

Article 300 General Requirements for Wiring Methods and Materials

Part I General Requirements

300.1 Scope

(A) All Wiring Installations

This article covers general requirements for wiring methods and materials for all wiring installations unless modified by other articles in Chapter 3.

(B) Integral Parts of Equipment

The provisions of this article are not intended to apply to the conductors that form an integral part of equipment, such as motors, controllers, motor control centers, or factory-assembled control equipment or listed utilization equipment.

(C) Metric Designators and Trade Sizes

Metric designators and trade sizes for conduit, tubing, and associated fittings and accessories shall be as designated in Table 300.1(C).

Table 300.1(C) Metric Designators and Trade Sizes

Metric Designator Trade Size

12 3/8

16 1/2

21 3/4

27 1

35 11/4

41 11/2

53 2

63 21/2

78 3

91 31/2

103 4

129 5

155 6

Note: The metric designators and trade sizes are for identification purposes only and are not actual dimensions.

300.2 Limitations

(A) Voltage

Wiring methods specified in Chapter 3 shall be used for 1000 volts, nominal, or less where not specifically limited in some section of Chapter 3. They shall be permitted for over 1000 volts, nominal, where specifically permitted elsewhere in this Code.

(B) Temperature

Temperature limitation of conductors shall be in accordance with 310.14(A)(3).

300.3 Conductors

(A) Single Conductors

Single conductors specified in Table 310.4(A) shall only be installed where part of a recognized wiring method of Chapter 3.

Exception: Individual conductors shall be permitted where installed as separate overhead conductors in accordance with 225.6.

(B) Conductors of the Same Circuit

All conductors of the same circuit and, where used, the grounded conductor and all equipment grounding conductors and bonding conductors shall be contained within the same raceway, auxiliary gutter, cable tray, cablebus assembly, trench, cable, or cord, unless otherwise permitted in accordance with 300.3(B)(1) through (B)(4).

(1) Paralleled Installations

Conductors shall be permitted to be run in parallel in accordance with the provisions of 310.10(G). The requirement to run all circuit conductors within the same raceway, auxiliary gutter, cable tray, trench, cable, or cord shall apply separately to each portion of the paralleled installation, and the equipment grounding conductors shall comply with 250.122. Connections, taps, or extensions made from paralleled conductors shall connect to all conductors of the paralleled set, grounded and ungrounded, as applicable. Parallel runs in cable trays shall comply with 392.20(C).

Exception: Conductors installed in nonmetallic raceways run underground shall be permitted to be arranged as isolated phase, neutral, and grounded conductor installations. The raceways shall be installed in close proximity, and the isolated phase, neutral, and grounded conductors shall comply with 300.20(B).

(2) Grounding and Bonding Conductors

Equipment grounding conductors shall be permitted to be installed outside a raceway or cable assembly where in accordance with the provisions of 250.130(C) for certain existing installations or in accordance with 250.134, Exception No. 2, for dc circuits. Equipment bonding conductors shall be permitted to be installed on the outside of raceways in accordance with 250.102(E).

(3) Nonferrous Wiring Methods

Conductors in wiring methods with a nonmetallic or other nonmagnetic sheath, where run in different raceways, auxiliary gutters, cable trays, trenches, cables, or cords, shall comply with 300.20(B). Conductors in single-conductor Type MI cable with a nonmagnetic sheath shall comply with 332.31. Conductors of single-conductor Type MC cable with a nonmagnetic sheath shall comply with 330.31, 330.116, and 300.20(B).

(4) Column-Width Panelboard Enclosures

Where an auxiliary gutter runs between a column-width panelboard and a pull box, and the pull box includes neutral terminations, the neutral conductors of circuits supplied from the panelboard shall be permitted to originate in the pull box.

(C) Conductors of Different Systems

(1) 1000 Volts, Nominal, or Less

Conductors of ac and dc circuits, rated 1000 volts, nominal, or less, shall be permitted to occupy the same equipment wiring enclosure, cable, or raceway. All conductors shall have an insulation rating equal to at least the maximum circuit voltage applied to any conductor within the enclosure, cable, or raceway.

Secondary wiring to electric-discharge lamps of 1000 volts or less, if insulated for the secondary voltage involved, shall be permitted to occupy the same luminaire, sign, or outline lighting enclosure as the branch-circuit conductors.

Informational Note No. 1: See 725.136(A) for Class 2 and Class 3 circuit conductors.

Informational Note No. 2: See 690.31(B) for photovoltaic source and output circuits.

(2) Over 1000 Volts, Nominal

Conductors of circuits rated over 1000 volts, nominal, shall not occupy the same equipment wiring enclosure, cable, or raceway with conductors of circuits rated 1000 volts, nominal, or less unless otherwise permitted in 300.3(C)(2)(a) through 300.3(C)(2)(d).

(a) Primary leads of electric-discharge lamp ballasts insulated for the primary voltage of the ballast, where contained within the individual wiring enclosure, shall be permitted to occupy the same luminaire, sign, or outline lighting enclosure as the branch-circuit conductors.

(b) Excitation, control, relay, and ammeter conductors used in connection with any individual motor or starter shall be permitted to occupy the same enclosure as the motor-circuit conductors.

(c) In motors, transformers, switchgear, switchboards, control assemblies, and similar equipment, conductors of different voltage ratings shall be permitted.

(d) In manholes, if the conductors of each system are permanently and effectively separated from the conductors of the other systems and securely fastened to racks, insulators, or other approved supports, conductors of different voltage ratings shall be permitted.

Conductors having nonshielded insulation and operating at different voltage levels shall not occupy the same enclosure, cable, or raceway.

300.4 Protection Against Physical Damage

Where subject to physical damage, conductors, raceways, and cables shall be protected.

(A) Cables and Raceways Through Wood Members

Upcodes Diagrams

(1) Bored Holes

In both exposed and concealed locations, where a cable- or raceway-type wiring method is installed through bored holes in joists, rafters, or wood members, holes shall be bored so that the edge of the hole is not less than 32 mm (11/4 in.) from the nearest edge of the wood member. Where this distance cannot be maintained, the cable or raceway shall be protected from penetration by screws or nails by a steel plate(s) or bushing(s), at least 1.6 mm (1/16 in.) thick, and of appropriate length and width installed to cover the area of the wiring.

Exception No. 1: Steel plates shall not be required to protect rigid metal conduit, intermediate metal conduit, rigid nonmetallic conduit, or electrical metallic tubing.

Exception No. 2: A listed and marked steel plate less than 1.6 mm (1/16 in.) thick that provides equal or better protection against nail or screw penetration shall be permitted.

(2) Notches in Wood

Where there is no objection because of weakening the building structure, in both exposed and concealed locations, cables or raceways shall be permitted to be laid in notches in wood studs, joists, rafters, or other wood members where the cable or raceway at those points is protected against nails or screws by a steel plate at least 1.6 mm (1/16 in.) thick, and of appropriate length and width, installed to cover the area of the wiring. The steel plate shall be installed before the building finish is applied.

Exception No. 1: Steel plates shall not be required to protect rigid metal conduit, intermediate metal conduit, rigid nonmetallic conduit, or electrical metallic tubing.

Exception No. 2: A listed and marked steel plate less than 1.6 mm (1/16 in.) thick that provides equal or better protection against nail or screw penetration shall be permitted.

(B) Nonmetallic-Sheathed Cables and Electrical Nonmetallic Tubing Through Metal Framing Members

(1) Nonmetallic-Sheathed Cable

In both exposed and concealed locations where nonmetallic-sheathed cables pass through either factory- or field-punched, cut, or drilled slots or holes in metal members, the cable shall be protected by listed bushings or listed grommets covering all metal edges that are securely fastened in the opening prior to installation of the cable.

(2) Nonmetallic-Sheathed Cable and Electrical Nonmetallic Tubing

Where nails or screws are likely to penetrate nonmetallic-sheathed cable or electrical nonmetallic tubing, a steel sleeve, steel plate, or steel clip not less than 1.6 mm (1/16 in.) in thickness shall be used to protect the cable or tubing.

Exception: A listed and marked steel plate less than 1.6 mm (1/16 in.) thick that provides equal or better protection against nail or screw penetration shall be permitted.

(C) Cables Through Spaces Behind Panels Designed to Allow Access

Cables or raceway-type wiring methods, installed behind panels designed to allow access, shall be supported according to their applicable articles.

(D) Cables and Raceways Parallel to Framing Members and Furring Strips

In both exposed and concealed locations, where a cable- or raceway-type wiring method is installed parallel to framing members, such as joists, rafters, or studs, or is installed parallel to furring strips, the cable or raceway shall be installed and supported so that the nearest outside surface of the cable or raceway is not less than 32 mm (11/4 in.) from the nearest edge of the framing member or furring strips where nails or screws are likely to penetrate. Where this distance cannot be maintained, the cable or raceway shall be protected from penetration by nails or screws by a steel plate, sleeve, or equivalent at least 1.6 mm (1/16 in.) thick.

Exception No. 1: Steel plates, sleeves, or the equivalent shall not be required to protect rigid metal conduit, intermediate metal conduit, rigid nonmetallic conduit, or electrical metallic tubing.

Exception No. 2: For concealed work in finished buildings, or finished panels for prefabricated buildings where such supporting is impracticable, it shall be permissible to fish the cables between access points.

Exception No. 3: A listed and marked steel plate less than 1.6 mm (1/16 in.) thick that provides equal or better protection against nail or screw penetration shall be permitted.

(E) Cables, Raceways, or Boxes Installed in or Under Roof Decking

A cable, raceway, or box, installed in exposed or concealed locations under metal-corrugated sheet roof decking, shall be installed and supported so there is not less than 38 mm (11/2 in.) measured from the lowest surface of the roof decking to the top of the cable, raceway, or box. A cable, raceway, or box shall not be installed in concealed locations in metal-corrugated, sheet decking—type roof.

Informational Note: Roof decking material is often repaired or replaced after the initial raceway or cabling and roofing installation and may be penetrated by the screws or other mechanical devices designed to provide "hold down" strength of the waterproof membrane or roof insulating material.

Exception: Rigid metal conduit and intermediate metal conduit shall not be required to comply with 300.4(E).

(F) Cables and Raceways Installed in Shallow Grooves

Cable- or raceway-type wiring methods installed in a groove, to be covered by wallboard, siding, paneling, carpeting, or similar finish, shall be protected by 1.6 mm (1/16 in.) thick steel plate, sleeve, or equivalent or by not less than 32-mm (11/4-in.) free space for the full length of the groove in which the cable or raceway is installed.

Exception No. 1: Steel plates, sleeves, or the equivalent shall not be required to protect rigid metal conduit, intermediate metal conduit, rigid nonmetallic conduit, or electrical metallic tubing.

Exception No. 2: A listed and marked steel plate less than 1.6 mm (1/16 in.) thick that provides equal or better protection against nail or screw penetration shall be permitted.

(G) Fittings

Where raceways contain 4 AWG or larger insulated circuit conductors, and these conductors enter a cabinet, a box, an enclosure, or a raceway, the conductors shall be protected in accordance with any of the following:

An identified fitting providing a smoothly rounded insulating surface

A listed metal fitting that has smoothly rounded edges

Separation from the fitting or raceway using an identified insulating material that is securely fastened in place

Threaded hubs or bosses that are an integral part of a cabinet, box, enclosure, or raceway providing a smoothly rounded or flared entry for conductors

Conduit bushings constructed wholly of insulating material shall not be used to secure a fitting or raceway. The insulating fitting or insulating material shall have a temperature rating not less than the insulation temperature rating of the installed conductors.

(H) Structural Joints

A listed expansion/deflection fitting or other approved means shall be used where a raceway crosses a structural joint intended for expansion, contraction or deflection, used in buildings, bridges, parking garages, or other structures.

300.5 Underground Installations

Table 300.5 Minimum Cover Requirements, 0 to 1000 Volts, Nominal, Burial in Millimeters (Inches)

Location of Wiring Method or Circuit Type of Wiring Method or Circuit

Column 1 Direct Burial Cables or Conductors Column 2 Rigid Metal Conduit or Intermediate Metal Conduit Column 3 Nonmetallic Raceways Listed for Direct Burial Without Concrete Encasement or Other Approved Raceways Column 4 Residential Branch Circuits Rated 120 Volts or Less with GFCI Protection and Maximum Overcurrent Protection of 20 Amperes Column 5 Circuits for Control of Irrigation and Landscape Lighting Limited to Not More Than 30 Volts and Installed with Type UF or in Other Identified Cable or Raceway

mm in. mm in. mm in. mm in. mm in.

All locations not specified below 600 24 150 6 450 18 300 12 150a, b 6a, b

In trench below 50 mm (2 in.) thick concrete or equivalent 450 18 150 6 300 12 150 6 150 6

Under a building 0 0 0 0 0 0 0 0 0 0

(in raceway or Type MC or Type MI cable identified for direct burial) (in raceway or Type MC or Type MI cable identified for direct burial) (in raceway or Type MC or Type MI cable identified for direct burial)

Under minimum of 102 mm (4 in.) thick concrete exterior slab with no vehicular traffic and the slab extending not less than 152 mm (6 in.) beyond the underground installation 450 18 100 4 100 4 150 6 150 6

(direct burial) (direct burial)

100 4 100 4

(in raceway) (in raceway)

Under streets, highways, roads, alleys, driveways, and parking lots 600 24 600 24 600 24 600 24 600 24

One- and two-family dwelling driveways and outdoor parking areas, and used only for dwelling-related purposes 450 18 450 18 450 18 300 12 450 18

In or under airport runways, including adjacent areas where trespassing prohibited 450 18 450 18 450 18 450 18 450 18

aA lesser depth shall be permitted where specified in the installation instructions of a listed low-voltage lighting system.

bA depth of 150 mm (6 in.) shall be permitted for pool, spa, and fountain lighting, installed in a nonmetallic raceway, limited to not more than 30 volts where part of a listed low-voltage lighting system.

Notes:

1. Cover is defined as the shortest distance in mm (in.) measured between a point on the top surface of any direct-buried conductor, cable, conduit, or other raceway and the top surface of finished grade, concrete, or similar cover.

2. Raceways approved for burial only where concrete encased shall require concrete envelope not less than 50 mm (2 in.) thick.

3. Lesser depths shall be permitted where cables and conductors rise for terminations or splices or where access is otherwise required.

4. Where one of the wiring method types listed in Columns 1 through 3 is used for one of the circuit types in Columns 4 and 5, the shallowest depth of burial shall be permitted.

5. Where solid rock prevents compliance with the cover depths specified in this table, the wiring shall be installed in a metal raceway, or a nonmetallic raceway permitted for direct burial. The raceways shall be covered by a minimum of 50 mm (2 in.) of concrete extending down to rock.

(A) Minimum Cover Requirements

Direct-buried cable, conduit, or other raceways shall be installed to meet the minimum cover requirements of Table 300.5.

(B) Wet Locations

The interior of enclosures or raceways installed underground shall be considered to be a wet location. Insulated conductors and cables installed in these enclosures or raceways in underground installations shall comply with 310.10(C).

(C) Underground Cables and Conductors Under Buildings

Underground cable and conductors installed under a building shall be in a raceway.

Exception No. 1: Type MI cable shall be permitted under a building without installation in a raceway where embedded in concrete, fill, or other masonry in accordance with 332.10(6) or in underground runs where suitably protected against physical damage and corrosive conditions in accordance with 332.10(10).

Exception No. 2: Type MC cable listed for direct burial or concrete encasement shall be permitted under a building without installation in a raceway in accordance with 330.10(A)(5) and in wet locations in accordance with 330.10(A)(11).

(D) Protection From Damage

Direct-buried conductors and cables shall be protected from damage in accordance with 300.5(D)(1) through (D)(4).

(1) Emerging From Grade

Direct-buried conductors and cables emerging from grade and specified in columns 1 and 4 of Table 300.5 shall be protected by enclosures or raceways extending from the minimum cover distance below grade required by 300.5(A) to a point at least 2.5 m (8 ft) above finished grade. In no case shall the protection be required to exceed 450 mm (18 in.) below finished grade.

(2) Conductors Entering Buildings

Conductors entering a building shall be protected to the point of entrance.

(3) Service Conductors

Underground service conductors that are not encased in concrete and that are buried 450 mm (18 in.) or more below grade shall have their location identified by a warning ribbon that is placed in the trench at least 300 mm (12 in.) above the underground installation.

(4) Enclosure or Raceway Damage

Where the enclosure or raceway is subject to physical damage, the conductors shall be installed in electrical metallic tubing, rigid metal conduit, intermediate metal conduit, RTRC-XW, Schedule 80 PVC conduit, or equivalent.

(E) Splices and Taps

Direct-buried conductors or cables shall be permitted to be spliced or tapped without the use of splice boxes. The splices or taps shall be made in accordance with 110.14(B).

(F) Backfill

Backfill that contains large rocks, paving materials, cinders, large or sharply angular substances, or corrosive material shall not be placed in an excavation where materials may damage raceways, cables, conductors, or other substructures or prevent adequate compaction of fill or contribute to corrosion of raceways, cables, or other substructures.

Where necessary to prevent physical damage to the raceway, cable, or conductor, protection shall be provided in the form of granular or selected material, suitable running boards, suitable sleeves, or other approved means.

(G) Raceway Seals

Conduits or raceways through which moisture may contact live parts shall be sealed or plugged at either or both ends. Spare or unused raceways shall also be sealed. Sealants shall be identified for use with the cable insulation, conductor insulation, bare conductor, shield, or other components.

Informational Note: Presence of hazardous gases or vapors may also necessitate sealing of underground conduits or raceways entering buildings.

(H) Bushing

A bushing, or terminal fitting, with an integral bushed opening shall be used at the end of a conduit or other raceway that terminates underground where the conductors or cables emerge as a direct burial wiring method. A seal incorporating the physical protection characteristics of a bushing shall be permitted to be used in lieu of a bushing.

(I) Conductors of the Same Circuit

All conductors of the same circuit and, where used, the grounded conductor and all equipment grounding conductors shall be installed in the same raceway or cable or shall be installed in close proximity in the same trench.

Exception No. 1: Conductors shall be permitted to be installed in parallel in raceways, multiconductor cables, or direct-buried single conductor cables. Each raceway or multiconductor cable shall contain all conductors of the same circuit, including equipment grounding conductors. Each direct-buried single conductor cable shall be located in close proximity in the trench to the other single conductor cables in the same parallel set of conductors in the circuit, including equipment grounding conductors.

Exception No. 2: Isolated phase, polarity, grounded conductor, and equipment grounding and bonding conductor installations shall be permitted in nonmetallic raceways or cables with a nonmetallic covering or nonmagnetic sheath in close proximity where conductors are paralleled as permitted in 310.10(G), and where the conditions of 300.20(B) are met.

(J) Earth Movement

Where direct-buried conductors, raceways, or cables are subject to movement by settlement or frost, direct-buried conductors, raceways, or cables shall be arranged so as to prevent damage to the enclosed conductors or to equipment connected to the raceways.

Informational Note: This section recognizes "S" loops in underground direct burial cables and conductors to raceway transitions, expansion fittings in raceway risers to fixed equipment, and, generally, the provision of flexible connections to equipment subject to settlement or frost heaves.

(K) Directional Boring

Cables or raceways installed using directional boring equipment shall be approved for the purpose.

300.6 Protection Against Corrosion and Deterioration

Raceways, cable trays, cablebus, auxiliary gutters, cable armor, boxes, cable sheathing, cabinets, elbows, couplings, fittings, supports, and support hardware shall be of materials suitable for the environment in which they are to be installed.

(A) Ferrous Metal Equipment

Ferrous metal raceways, cable trays, cablebus, auxiliary gutters, cable armor, boxes, cable sheathing, cabinets, metal elbows, couplings, nipples, fittings, supports, and support hardware shall be suitably protected against corrosion inside and outside (except threads at joints) by a coating of approved corrosion-resistant material. Where corrosion protection is necessary and the conduit is threaded in the field, the threads shall be coated with an approved electrically conductive, corrosion-resistant compound.

Informational Note: Field-cut threads are those threads that are cut in conduit, elbows, or nipples anywhere other than at the factory where the product is listed.

Exception: Stainless steel shall not be required to have protective coatings.

(1) Protected From Corrosion Solely by Enamel

Where protected from corrosion solely by enamel, ferrous metal raceways, cable trays, cablebus, auxiliary gutters, cable armor, boxes, cable sheathing, cabinets, metal elbows, couplings, nipples, fittings, supports, and support hardware shall not be used outdoors or in wet locations as described in 300.6(D).

(2) Organic Coatings on Boxes or Cabinets

Where boxes or cabinets have an approved system of organic coatings and are marked "Raintight," "Rainproof," or "Outdoor Type," they shall be permitted outdoors.

(3) In Concrete or in Direct Contact With the Earth

Ferrous metal raceways, cable armor, boxes, cable sheathing, cabinets, elbows, couplings, nipples, fittings, supports, and support hardware shall be permitted to be installed in concrete or in direct contact with the earth, or in areas subject to severe corrosive influences where made of material approved for the condition, or where provided with corrosion protection approved for the condition.

(B) Aluminum Metal Equipment

Aluminum raceways, cable trays, cablebus, auxiliary gutters, cable armor, boxes, cable sheathing, cabinets, elbows, couplings, nipples, fittings, supports, and support hardware embedded or encased in concrete or in direct contact with the earth shall be provided with supplementary corrosion protection.

(C) Nonmetallic Equipment

Nonmetallic raceways, cable trays, cablebus, auxiliary gutters, boxes, cables with a nonmetallic outer jacket and internal metal armor or jacket, cable sheathing, cabinets, elbows, couplings, nipples, fittings, supports, and support hardware shall be made of material approved for the condition and shall comply with 300.6(C)(1) and (C)(2) as applicable to the specific installation.

(1) Exposed to Sunlight

Where exposed to sunlight, the materials shall be listed as sunlight resistant or shall be identified as sunlight resistant.

(2) Chemical Exposure

Where subject to exposure to chemical solvents, vapors, splashing, or immersion, materials or coatings shall either be inherently resistant to chemicals based on their listing or be identified for the specific chemical reagent.

(D) Indoor Wet Locations

In portions of dairy processing facilities, laundries, canneries, and other indoor wet locations, and in locations where walls are frequently washed or where there are surfaces of absorbent materials, such as damp paper or wood, the entire wiring system, where installed exposed, including all boxes, fittings, raceways, and cable used therewith, shall be mounted so that there is at least a 6-mm (1/4-in.) airspace between it and the wall or supporting surface.

Exception: Nonmetallic raceways, boxes, and fittings shall be permitted to be installed without the airspace on a concrete, masonry, tile, or similar surface.

Informational Note: In general, areas where acids and alkali chemicals are handled and stored may present such corrosive conditions, particularly when wet or damp. Severe corrosive conditions may also be present in portions of meatpacking plants, tanneries, glue houses, and some stables; in installations immediately adjacent to a seashore and swimming pool areas; in areas where chemical deicers are used; and in storage cellars or rooms for hides, casings, fertilizer, salt, and bulk chemicals.

300.7 Raceways Exposed to Different Temperatures

(A) Sealing

Where portions of a raceway or sleeve are known to be subjected to different temperatures, and where condensation is known to be a problem, as in cold storage areas of buildings or where passing from the interior to the exterior of a building, the raceway or sleeve shall be sealed to prevent the circulation of warm air to a colder section of the raceway or sleeve. Sealants shall be identified for use with cable insulation, conductor insulation, a bare conductor, a shield, or other components. An explosionproof seal shall not be required for this purpose.

(B) Expansion, Expansion-Deflection, and Deflection Fittings

Raceways shall be provided with expansion, expansion-deflection, or deflection fittings where necessary to compensate for thermal expansion, deflection, and contraction.

Informational Note: Table 352.44 and Table 355.44 provide the expansion information for polyvinyl chloride (PVC) and for reinforced thermosetting resin conduit (RTRC), respectively. A nominal number for steel conduit can be determined by multiplying the expansion length in Table 352.44 by 0.20. The coefficient of expansion for steel electrical metallic tubing, intermediate metal conduit, and rigid metal conduit is 1.170 × 10—5 (0.0000117 mm per mm of conduit for each °C in temperature change) [0.650 × 10—5 (0.0000065 in. per inch of conduit for each °F in temperature change)].

A nominal number for aluminum conduit and aluminum electrical metallic tubing can be determined by multiplying the expansion length in Table 352.44 by 0.40. The coefficient of expansion for aluminum electrical metallic tubing and aluminum rigid metal conduit is 2.34 × 10—5 (0.0000234 mm per mm of conduit for each °C in temperature change) [1.30 × 10—5 (0.000013 in. per inch of conduit for each °F in temperature change)].

300.8 Installation of Conductors With Other Systems

Raceways or cable trays containing electrical conductors shall not contain any pipe, tube, or equal for steam, water, air, gas, drainage, or any service other than electrical.

300.9 Raceways in Wet Locations Abovegrade

Where raceways are installed in wet locations abovegrade, the interior of these raceways shall be considered to be a wet location. Insulated conductors and cables installed in raceways in wet locations abovegrade shall comply with 310.10(C).

300.10 Electrical Continuity of Metal Raceways and Enclosures

Metal raceways, cable armor, and other metal enclosures for conductors shall be metallically joined together into a continuous electrical conductor and shall be connected to all boxes, fittings, and cabinets so as to provide effective electrical continuity. Unless specifically permitted elsewhere in this Code, raceways and cable assemblies shall be mechanically secured to boxes, fittings, cabinets, and other enclosures.

Exception No. 1: Short sections of raceways used to provide support or protection of cable assemblies from physical damage shall not be required to be made electrically continuous.

Exception No. 2: Equipment enclosures to be isolated, as permitted by 250.96(B), shall not be required to be metallically joined to the metal raceway.

300.11 Securing and Supporting

(A) Secured in Place

Raceways, cable assemblies, boxes, cabinets, and fittings shall be securely fastened in place.

(B) Wiring Systems Installed Above Suspended Ceilings

Support wires that do not provide secure support shall not be permitted as the sole support. Support wires and associated fittings that provide secure support and that are installed in addition to the ceiling grid support wires shall be permitted as the sole support. Where independent support wires are used, they shall be secured at both ends. Cables and raceways shall not be supported by ceiling grids.

(1) Fire-Rated Assemblies

Wiring located within the cavity of a fire-rated floor—ceiling or roof—ceiling assembly shall not be secured to, or supported by, the ceiling assembly, including the ceiling support wires. An independent means of secure support shall be provided and shall be permitted to be attached to the assembly. Where independent support wires are used, they shall be distinguishable by color, tagging, or other effective means from those that are part of the fire-rated design.

Exception: The ceiling support system shall be permitted to support wiring and equipment that have been tested as part of the fire-rated assembly.

Informational Note: One method of determining fire rating is testing in accordance with ANSI/ASTM E119-18b, Standard Test Methods for Fire Tests of Building Construction and Materials.

(2) Non—Fire-Rated Assemblies

Wiring located within the cavity of a non-fire-rated floor—ceiling or roof—ceiling assembly shall not be secured to, or supported by, the ceiling assembly, including the ceiling support wires. An independent means of secure support shall be provided and shall be permitted to be attached to the assembly. Where independent support wires are used, they shall be distinguishable by color, tagging, or other effective means.

Exception: The ceiling support system shall be permitted to support branch-circuit wiring and associated equipment where installed in accordance with the ceiling system manufacturer's instructions.

(C) Raceways Used as Means of Support

Raceways shall be used only as a means of support for other raceways, cables, or nonelectrical equipment under any of the following conditions:

Where the raceway or means of support is identified as a means of support

Where the raceway contains power supply conductors for electrically controlled equipment and is used to support Class 2 circuit conductors or cables that are solely for the purpose of connection to the equipment control circuits

Where the raceway is used to support boxes or conduit bodies in accordance with 314.23 or to support luminaires in accordance with 410.36(E)

(D) Cables Not Used as Means of Support

Cable wiring methods shall not be used as a means of support for other cables, raceways, or nonelectrical equipment.

300.12 Mechanical Continuity — Raceways and Cables

Raceways, cable armors, and cable sheaths shall be continuous between cabinets, boxes, fittings, or other enclosures or outlets.

Exception No. 1: Short sections of raceways used to provide support or protection of cable assemblies from physical damage shall not be required to be mechanically continuous.

Exception No. 2: Raceways and cables installed into the bottom of open bottom equipment, such as switchboards, motor control centers, and floor or pad-mounted transformers, shall not be required to be mechanically secured to the equipment.

300.13 Mechanical and Electrical Continuity — Conductors

(A) General

Conductors in raceways shall be continuous between outlets, boxes, devices, and so forth. There shall be no splice or tap within a raceway unless permitted by 300.15, 368.56(A), 376.56, 378.56, 384.56, 386.56, 388.56, or 390.56.

(B) Device Removal

In multiwire branch circuits, the continuity of a grounded conductor shall not depend on device connections such as lampholders, receptacles, and so forth, where the removal of such devices would interrupt the continuity.

300.14 Length of Free Conductors at Outlets, Junctions, and Switch Points

At least 150 mm (6 in.) of free conductor, measured from the point in the box where it emerges from its raceway or cable sheath, shall be left at each outlet, junction, and switch point for splices or the connection of luminaires or devices. Where the opening to an outlet, junction, or switch point is less than 200 mm (8 in.) in any dimension, each conductor shall be long enough to extend at least 75 mm (3 in.) outside the opening.

Exception: Conductors that are not spliced or terminated at the outlet, junction, or switch point shall not be required to comply with 300.14.

300.15 Boxes, Conduit Bodies, or Fittings — Where Required

A box shall be installed at each outlet and switch point for concealed knob-and-tube wiring.

Fittings and connectors shall be used only with the specific wiring methods for which they are designed and listed.

Where the wiring method is conduit, tubing, Type AC cable, Type MC cable, Type MI cable, nonmetallic-sheathed cable, or other cables, a box or conduit body shall be installed at each conductor splice point, outlet point, switch point, junction point, termination point, or pull point, unless otherwise permitted in 300.15(A) through (L).

(A) Wiring Methods With Interior Access

A box or conduit body shall not be required for each splice, junction, switch, pull, termination, or outlet points in wiring methods with removable covers, such as wireways, multioutlet assemblies, auxiliary gutters, and surface raceways. The covers shall be accessible after installation.

(B) Equipment

An integral junction box or wiring compartment as part of approved equipment shall be permitted in lieu of a box.

(C) Protection

A box or conduit body shall not be required where cables enter or exit from conduit or tubing that is used to provide cable support or protection against physical damage. A fitting shall be provided on the end(s) of the conduit or tubing to protect the cable from abrasion.

(D) Type MI Cable

A box or conduit body shall not be required where accessible fittings are used for straight-through splices in mineral-insulated metal-sheathed cable.

(E) Integral Enclosure

A wiring device with integral enclosure identified for the use, having brackets that securely fasten the device to walls or ceilings of conventional on-site frame construction, for use with nonmetallic-sheathed cable, shall be permitted in lieu of a box or conduit body.

Informational Note: See 334.30(C); 545.10; 550.15(I); 551.47(E), Exception No. 1; and 552.48(E), Exception No. 1.

(F) Fitting

A fitting identified for the use shall be permitted in lieu of a box or conduit body where conductors are not spliced or terminated within the fitting. The fitting shall be accessible after installation, unless listed for concealed installation.

(G) Direct-Buried Conductors

As permitted in 300.5(E), a box or conduit body shall not be required for splices and taps in direct-buried conductors and cables.

(H) Insulated Devices

As permitted in 334.40(B), a box or conduit body shall not be required for insulated devices supplied by nonmetallic-sheathed cable.

(I) Enclosures

A box or conduit body shall not be required where a splice, switch, terminal, or pull point is in a cabinet or cutout box, in an enclosure for a switch or overcurrent device as permitted in 312.8, in a motor controller as permitted in 430.10(A), or in a motor control center.

(J) Luminaires

A box or conduit body shall not be required where a luminaire is used as a raceway as permitted in 410.64.

(K) Embedded

A box or conduit body shall not be required for splices where conductors are embedded as permitted in 424.40, 424.41(D), 426.22(C), 426.24(A), and 427.19(A).

(L) Manholes and Handhole Enclosures

A box or conduit body shall not be required for conductors in manholes or handhole enclosures, except where connecting to electrical equipment. The installation shall comply with the provisions of Part V of Article 110 for manholes, and 314.30 for handhole enclosures.

300.16 Raceway or Cable to Open or Concealed Wiring

(A) Box, Conduit Body, or Fitting

A box, conduit body, or terminal fitting having a separately bushed hole for each conductor shall be used wherever a change is made from conduit, electrical metallic tubing, electrical nonmetallic tubing, nonmetallic-sheathed cable, Type AC cable, Type MC cable, or mineral-insulated, metal-sheathed cable and surface raceway wiring to open wiring or to concealed knob-and-tube wiring. A fitting used for this purpose shall contain no taps or splices and shall not be used at luminaire outlets. A conduit body used for this purpose shall contain no taps or splices, unless it complies with 314.16(C)(2).

(B) Bushing

A bushing shall be permitted in lieu of a box or terminal where the conductors emerge from a raceway and enter or terminate at equipment, such as open switchboards, unenclosed control equipment, or similar equipment. The bushing shall be of the insulating type for other than lead-sheathed conductors.

300.17 Number and Size of Conductors in Raceway

The number and size of conductors in any raceway shall not be more than will permit dissipation of the heat and ready installation or withdrawal of the conductors without damage to the conductors or to their insulation.

Informational Note: See the following sections of this Code: intermediate metal conduit, 342.22; rigid metal conduit, 344.22; flexible metal conduit, 348.22; liquidtight flexible metal conduit, 350.22; PVC conduit, 352.22; HDPE conduit, 353.22; RTRC, 355.22; liquidtight nonmetallic flexible conduit, 356.22; electrical metallic tubing, 358.22; flexible metallic tubing, 360.22; electrical nonmetallic tubing, 362.22; cellular concrete floor raceways, 372.22; cellular metal floor raceways, 374.22; metal wireways, 376.22; nonmetallic wireways, 378.22; surface metal raceways, 386.22; surface nonmetallic raceways, 388.22; underfloor raceways, 390.22; fixture wire, 402.7; theaters, 520.6; signs, 600.31(C); elevators, 620.33; audio signal processing, amplification, and reproduction equipment, 640.23(A) and 640.24; Class 1, Class 2, and Class 3 circuits, Article 725; fire alarm circuits, Article 760; and optical fiber cables and raceways, Article 770.

300.18 Raceway Installations

(A) Complete Runs

Raceways, other than busways or exposed raceways having hinged or removable covers, shall be installed complete between outlet, junction, or splicing points prior to the installation of conductors. Where required to facilitate the installation of utilization equipment, the raceway shall be permitted to be initially installed without a terminating connection at the equipment. Prewired raceway assemblies shall be permitted only where specifically permitted in this Code for the applicable wiring method.

Exception: Short sections of raceways used to contain conductors or cable assemblies for protection from physical damage shall not be required to be installed complete between outlet, junction, or splicing points.

(B) Welding

Metal raceways shall not be supported, terminated, or connected by welding to the raceway unless specifically designed to be or otherwise specifically permitted to be in this Code.

300.19 Supporting Conductors in Vertical Raceways

(A) Spacing Intervals — Maximum

Conductors in vertical raceways shall be supported if the vertical rise exceeds the values in Table 300.19(A). At least one support method shall be provided for each conductor at the top of the vertical raceway or as close to the top as practical. Intermediate supports shall be provided as necessary to limit supported conductor lengths to not greater than those values specified in Table 300.19(A).

Exception: Steel wire armor cable shall be supported at the top of the riser with a cable support that clamps the steel wire armor. A safety device shall be permitted at the lower end of the riser to hold the cable in the event there is slippage of the cable in the wire-armored cable support. Additional wedge-type supports shall be permitted to relieve the strain on the equipment terminals caused by expansion of the cable under load.

Table 300.19(A) Spacings for Conductor Supports

Conductor Size Support of Conductors in Vertical Raceways Conductors

Aluminum or Copper-Clad Aluminum Copper

m ft m ft

18 AWG through 8 AWG Not greater than 30 100 30 100

6 AWG through 1/0 AWG Not greater than 60 200 30 100

2/0 AWG through 4/0 AWG Not greater than 55 180 25 80

Over 4/0 AWG through 350 kcmil Not greater than 41 135 18 60

Over 350 kcmil through 500 kcmil Not greater than 36 120 15 50

Over 500 kcmil through 750 kcmil Not greater than 28 95 12 40

Over 750 kcmil Not greater than 26 85 11 35

(B) Fire-Rated Cables and Conductors

Support methods and spacing intervals for fire-rated cables and conductors shall comply with any restrictions provided in the listing of the electrical circuit protective system used and in no case shall exceed the values in Table 300.19(A).

(C) Support Methods

One of the following methods of support shall be used:

Clamping devices constructed of or employing insulating wedges inserted in the ends of the raceways. Where clamping of insulation does not adequately support the cable, the conductor also shall be clamped.

Inserting boxes at the required intervals in which insulating supports are installed and secured in an approved manner to withstand the weight of the conductors attached thereto, the boxes being provided with covers.

In junction boxes, deflecting the cables not less than 90 degrees and carrying them horizontally to a distance not less than twice the diameter of the cable, the cables being carried on two or more insulating supports and additionally secured thereto by tie wires, if desired. Where this method is used, cables shall be supported at intervals not greater than 20 percent of the support spacing in Table 300.19(A).

Other approved means.

300.20 Induced Currents in Ferrous Metal Enclosures or Ferrous Metal Raceways

(A) Conductors Grouped Together

Where conductors carrying alternating current are installed in ferrous metal enclosures or ferrous metal raceways, they shall be arranged so as to avoid heating the surrounding ferrous metal by induction. To accomplish this, all phase conductors and, where used, the grounded conductor and all equipment grounding conductors shall be grouped together.

Exception No. 1: Equipment grounding conductors for certain existing installations shall be permitted to be installed separate from their associated circuit conductors where run in accordance with the provisions of 250.130(C).

Exception No. 2: A single conductor shall be permitted to be installed in a ferromagnetic enclosure and used for skin-effect heating in accordance with the provisions of 426.42 and 427.47.

(B) Individual Conductors

Where a single conductor carrying alternating current passes through metal with magnetic properties, the inductive effect shall be minimized by (1) cutting slots in the metal between the individual holes through which the individual conductors pass or (2) passing all the conductors in the circuit through an insulating wall sufficiently large for all of the conductors of the circuit.

Exception: In the case of circuits supplying vacuum or electric-discharge lighting systems or signs or X-ray apparatus, the currents carried by the conductors are so small that the inductive heating effect can be ignored where these conductors are placed in metal enclosures or pass through metal.

Informational Note: Because aluminum is not a magnetic metal, there will be no heating due to hysteresis; however, induced currents will be present. They will not be of sufficient magnitude to require grouping of conductors or special treatment in passing conductors through aluminum wall sections.

300.21 Spread of Fire or Products of Combustion

Electrical installations in hollow spaces, vertical shafts, and ventilation or air-handling ducts shall be made so that the possible spread of fire or products of combustion will not be substantially increased. Openings around electrical penetrations into or through fire-resistant-rated walls, partitions, floors, or ceilings shall be firestopped using approved methods to maintain the fire resistance rating.

Informational Note: Directories of electrical construction materials published by qualified testing laboratories contain many listing installation restrictions necessary to maintain the fire-resistive rating of assemblies where penetrations or openings are made. Building codes also contain restrictions on membrane penetrations on opposite sides of a fire-resistance-rated wall assembly. An example is the 600-mm (24-in.) minimum horizontal separation that usually applies between boxes installed on opposite sides of the wall. Assistance in complying with 300.21 can be found in building codes, fire resistance directories, and product listings.

300.22 Wiring in Ducts Not Used for Air Handling, Fabricated Ducts for Environmental Air, and Other Spaces for Environmental Air (Plenums)

The provisions of this section shall apply to the installation and uses of electrical wiring and equipment in ducts used for dust, loose stock, or vapor removal; ducts specifically fabricated for environmental air; and other spaces used for environmental air (plenums).

Informational Note: See Article 424, Part VI, for duct heaters.

(A) Ducts for Dust, Loose Stock, or Vapor Removal

No wiring systems of any type shall be installed in ducts used to transport dust, loose stock, or flammable vapors. No wiring system of any type shall be installed in any duct, or shaft containing only such ducts, used for vapor removal or for ventilation of commercial-type cooking equipment.

(B) Ducts Specifically Fabricated for Environmental Air

Equipment, devices, and the wiring methods specified in this section shall be permitted within such ducts only if necessary for the direct action upon, or sensing of, the contained air. Where equipment or devices are installed and illumination is necessary to facilitate maintenance and repair, enclosed gasketed-type luminaires shall be permitted.

Only wiring methods consisting of Type MI cable without an overall nonmetallic covering, Type MC cable employing a smooth or corrugated impervious metal sheath without an overall nonmetallic covering, electrical metallic tubing, flexible metallic tubing, intermediate metal conduit, or rigid metal conduit without an overall nonmetallic covering shall be installed in ducts specifically fabricated to transport environmental air. Flexible metal conduit shall be permitted, in lengths not to exceed 1.2 m (4 ft), to connect physically adjustable equipment and devices permitted to be in these fabricated ducts. The connectors used with flexible metal conduit shall effectively close any openings in the connection.

Exception: Wiring methods and cabling systems, listed for use in other spaces used for environmental air (plenums), shall be permitted to be installed in ducts specifically fabricated for environmental air-handling purposes under the following conditions:

The wiring methods or cabling systems shall be permitted only if necessary to connect to equipment or devices associated with the direct action upon or sensing of the contained air, and

The total length of such wiring methods or cabling systems shall not exceed 1.2 m (4 ft).

(C) Other Spaces Used for Environmental Air (Plenums)

This section shall apply to spaces not specifically fabricated for environmental air-handling purposes but used for air-handling purposes as a plenum. This section shall not apply to habitable rooms or areas of buildings, the prime purpose of which is not air handling.

Informational Note No. 1: The space over a hung ceiling used for environmental air-handling purposes is an example of the type of other space to which this section applies.

Informational Note No. 2: The phrase other spaces used for environmental air (plenum) as used in this section correlates with the use of the term plenum in NFPA 90A-2018, Standard for the Installation of Air-Conditioning and Ventilating Systems, and other mechanical codes where the plenum is used for return air purposes, as well as some other air-handling spaces.

Exception: This section shall not apply to the joist or stud spaces of dwelling units where the wiring passes through such spaces perpendicular to the long dimension of such spaces.

(1) Wiring Methods

The wiring methods for such other space shall be limited to totally enclosed, nonventilated, insulated busway having no provisions for plug-in connections, Type MI cable without an overall nonmetallic covering, Type MC cable without an overall nonmetallic covering, Type AC cable, or other factory-assembled multiconductor control or power cable that is specifically listed for use within an air-handling space, or listed prefabricated cable assemblies of metallic manufactured wiring systems without nonmetallic sheath. Other types of cables, conductors, and raceways shall be permitted to be installed in electrical metallic tubing, flexible metallic tubing, intermediate metal conduit, rigid metal conduit without an overall nonmetallic covering, flexible metal conduit, or, where accessible, surface metal raceway or metal wireway with metal covers.

Nonmetallic cable ties and other nonmetallic cable accessories used to secure and support cables shall be listed as having low smoke and heat release properties.

Informational Note: One method to determine low smoke and heat release properties is that the nonmetallic cable ties and other nonmetallic cable accessories exhibit a maximum peak optical density of 0.50 or less, an average optical density of 0.15 or less, and a peak heat release rate of 100 kW or less when tested in accordance with ANSI/UL 2043-2008, Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces.

(2) Cable Tray Systems

The provisions in 300.22(C)(2)(a) or (C)(2)(b) shall apply to the use of metallic cable tray systems in other spaces used for environmental air (plenums), where accessible, as follows:

(a) Metal Cable Tray Systems. Metal cable tray systems shall be permitted to support the wiring methods in 300.22(C)(1).

(b) Solid Side and Bottom Metal Cable Tray Systems. Solid side and bottom metal cable tray systems with solid metal covers shall be permitted to enclose wiring methods and cables, not already covered in 300.22(C)(1), in accordance with 392.10(A) and (B).

(3) Equipment

Electrical equipment with a metal enclosure, or electrical equipment with a nonmetallic enclosure listed for use within an air-handling space and having low smoke and heat release properties, and associated wiring material suitable for the ambient temperature shall be permitted to be installed in such other space unless prohibited elsewhere in this Code.

Informational Note: One method to determine low smoke and heat release properties is that the equipment exhibits a maximum peak optical density of 0.50 or less, an average optical density of 0.15 or less, and a peak heat release rate of 100 kW or less when tested in accordance with ANSI/UL 2043-2013, Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces.

Exception: Integral fan systems shall be permitted where specifically identified for use within an air-handling space.

(D) Information Technology Equipment

Where the installation complies with the special requirements in 645.4, electrical wiring in air-handling areas beneath raised floors for information technology equipment shall be permitted in accordance with 645.5(E).

300.23 Panels Designed to Allow Access

Cables, raceways, and equipment installed behind panels designed to allow access, including suspended ceiling panels, shall be arranged and secured so as to allow the removal of panels and access to the equipment.

300.25 Exit Enclosures (Stair Towers)

Where an exit enclosure is required to be separated from the building, only electrical wiring methods serving equipment permitted by the authority having jurisdiction in the exit enclosure shall be installed within the exit enclosure.

Informational Note: For more information, refer to NFPA 101-2018, Life Safety Code, 7.1.3.2.1(10)(b).

Part II Requirements for Over 1000 Volts, Nominal

300.31 Covers Required

Suitable covers shall be installed on all boxes, fittings, and similar enclosures to prevent accidental contact with energized parts or physical damage to parts or insulation.

300.32 Conductors of Different Systems

See 300.3(C)(2).

300.34 Conductor Bending Radius

The conductor shall not be bent to a radius less than 8 times the overall diameter for nonshielded conductors or 12 times the overall diameter for shielded or lead-covered conductors during or after installation. For multiconductor or multiplexed single-conductor cables having individually shielded conductors, the minimum bending radius is 12 times the diameter of the individually shielded conductors or 7 times the overall diameter, whichever is greater.

300.35 Protection Against Induction Heating

Metallic raceways and associated conductors shall be arranged so as to avoid heating of the raceway in accordance with the applicable provisions of 300.20.

300.37 Aboveground Wiring Methods

Aboveground conductors shall be installed in rigid metal conduit, in intermediate metal conduit, in electrical metallic tubing, in RTRC and PVC conduit, in cable trays, in auxiliary gutters, as busways, as cablebus, in other identified raceways, or as exposed runs of metal-clad cable suitable for the use and purpose. In locations accessible to qualified persons only, exposed runs of Type MV cables, bare conductors, and bare busbars shall also be permitted. Busbars shall be permitted to be either copper or aluminum.

Exception: Airfield lighting cable used in series circuits that are powered by regulators and installed in restricted airport lighting vaults shall be permitted as exposed cable installations.

Informational Note: FAA L-824 cables installed as exposed runs within a restricted vault area are common applications.

300.38 Raceways in Wet Locations Above Grade

Where raceways are installed in wet locations above grade, the interior of these raceways shall be considered to be a wet location. Insulated conductors and cables installed in raceways in wet locations above grade shall comply with 310.10(C).

300.39 Braid-Covered Insulated Conductors — Exposed Installation

Exposed runs of braid-covered insulated conductors shall have a flame-retardant braid. If the conductors used do not have this protection, a flame-retardant saturant shall be applied to the braid covering after installation. This treated braid covering shall be stripped back a safe distance at conductor terminals, according to the operating voltage. Where practicable, this distance shall not be less than 25 mm (1 in.) for each kilovolt of the conductor-to-ground voltage of the circuit.

300.40 Insulation Shielding

Metallic and semiconducting insulation shielding components of shielded cables shall be removed for a distance dependent on the circuit voltage and insulation. Stress reduction means shall be provided at all terminations of factory-applied shielding.

Metallic shielding components such as tapes, wires, or braids, or combinations thereof, shall be connected to an equipment grounding conductor, an equipment grounding busbar, or a grounding electrode.

300.42 Moisture or Mechanical Protection for Metal-Sheathed Cables

Where cable conductors emerge from a metal sheath and where protection against moisture or physical damage is necessary, the insulation of the conductors shall be protected by a cable sheath terminating device.

300.45 Danger Signs

Danger signs shall be conspicuously posted at points of access to conductors in all raceway systems and cable systems. The sign(s) shall meet the requirements in 110.21(B), shall be readily visible, and shall state the following:

DANGER—HIGH VOLTAGE—KEEP OUT

300.50 Underground Installations

Table 300.50 Minimum Covera Requirements

Circuit Voltage General Conditions (not otherwise specified) Special Conditions (use if applicable)

Column 1 Column 2 Column 3 Column 4 Column 5 Column 6

Direct-Buried Cablesb RTRC, PVC, and HDPE Conduitc Rigid Metal Conduit and Intermediate Metal Conduit Raceways Under Buildings or Exterior Concrete Slabs, 100 mm (4 in.) Minimum Thicknessd Cables in Airport Runways or Adjacent Areas Where Trespass Is Prohibited Areas Subject to Vehicular Traffic, Such as Thoroughfares and Commercial Parking Areas

mm in. mm in. mm in. mm in. mm in. mm in.

Over 1000 V through 22 kV 750 30 450 18 150 6 100 4 450 18 600 24

Over 22 kV through 40 kV 900 36 600 24 150 6 100 4 450 18 600 24

Over 40 kV 1000 42 750 30 150 6 100 4 450 18 600 24

General Notes:

1. Lesser depths shall be permitted where cables and conductors rise for terminations or splices or where access is otherwise required.

2. Where solid rock prevents compliance with the cover depths specified in this table, the wiring shall be installed in a metal or nonmetallic raceway permitted for direct burial. The raceways shall be covered by a minimum of 50 mm (2 in.) of concrete extending down to rock.

3. In industrial establishments, where conditions of maintenance and supervision ensure that qualified persons will service the installation, the minimum cover requirements, for other than rigid metal conduit and intermediate metal conduit, shall be permitted to be reduced 150 mm (6 in.) for each 50 mm (2 in.) of concrete or equivalent placed entirely within the trench over the underground installation.

Specific Footnotes:

aCover is defined as the shortest distance in millimeters (inches) measured between a point on the top surface of any direct-buried conductor, cable, conduit, or other raceway and the top surface of finished grade, concrete, or similar cover.

bUnderground direct-buried cables that are not encased or protected by concrete and are buried 750 mm (30 in.) or more below grade shall have their location identified by a warning ribbon that is placed in the trench at least 300 mm (12 in.) above the cables.

cListed by a qualified testing agency as suitable for direct burial without encasement. All other nonmetallic systems shall require 50 mm (2 in.) of concrete or equivalent above conduit in addition to the table depth.

dThe slab shall extend a minimum of 150 mm (6 in.) beyond the underground installation, and a warning ribbon or other effective means suitable for the conditions shall be placed above the underground installation.

(A) General

Underground conductors shall be identified for the voltage and conditions under which they are installed. Direct-burial cables shall comply with the provisions of 310.10(E). Underground cables shall be installed in accordance with 300.50(A)(1), (A)(2), or (A)(3), and the installation shall meet the depth requirements of Table 300.50.

(1) Shielded Cables and Nonshielded Cables in Metal-Sheathed Cable Assemblies

Underground cables, including nonshielded, Type MC and moisture-impervious metal sheath cables, shall have those sheaths grounded through an effective grounding path meeting the requirements of 250.4(A)(5) or (B)(4). They shall be direct buried or installed in raceways identified for the use.

(2) Industrial Establishments

In industrial establishments, where conditions of maintenance and supervision ensure that only qualified persons service the installed cable, nonshielded single-conductor cables with insulation types up to 2000 volts that are listed for direct burial shall be permitted to be directly buried.

(3) Other Nonshielded Cables

Other nonshielded cables not covered in 300.50(A)(1) or (A)(2) shall be installed in rigid metal conduit, intermediate metal conduit, or rigid nonmetallic conduit encased in not less than 75 mm (3 in.) of concrete.

(B) Wet Locations

The interior of enclosures or raceways installed underground shall be considered to be a wet location. Insulated conductors and cables installed in these enclosures or raceways in underground installations shall be listed for use in wet locations and shall comply with 310.10(C). Any connections or splices in an underground installation shall be approved for wet locations.

(C) Protection From Damage

Conductors emerging from the ground shall be enclosed in listed raceways. Raceways installed on poles shall be of rigid metal conduit, intermediate metal conduit, RTRC-XW, Schedule 80 PVC conduit, or equivalent, extending from the minimum cover depth specified in Table 300.50 to a point 2.5 m (8 ft) above finished grade. Conductors entering a building shall be protected by an approved enclosure or raceway from the minimum cover depth to the point of entrance. Where direct-buried conductors, raceways, or cables are subject to movement by settlement or frost, they shall be installed to prevent damage to the enclosed conductors or to the equipment connected to the raceways. Metallic enclosures shall be grounded.

(D) Splices

Direct burial cables shall be permitted to be spliced or tapped without the use of splice boxes, provided they are installed using materials suitable for the application. The taps and splices shall be watertight and protected from mechanical damage. Where cables are shielded, the shielding shall be continuous across the splice or tap.

Exception: At splices of an engineered cabling system, metallic shields of direct-buried single-conductor cables with maintained spacing between phases shall be permitted to be interrupted and overlapped. Where shields are interrupted and overlapped, each shield section shall be grounded at one point.

(E) Backfill

Backfill containing large rocks, paving materials, cinders, large or sharply angular substances, or corrosive materials shall not be placed in an excavation where materials can damage or contribute to the corrosion of raceways, cables, or other substructures or where it may prevent adequate compaction of fill.

Protection in the form of granular or selected material or suitable sleeves shall be provided to prevent physical damage to the raceway or cable.

(F) Raceway Seal

Where a raceway enters from an underground system, the end within the building shall be sealed with an identified compound so as to prevent the entrance of moisture or gases, or it shall be so arranged to prevent moisture from contacting live parts.

Article 310 Conductors for General Wiring

Part I General

310.1 Scope

This article covers general requirements for conductors rated up to and including 2000 volts and their type designations, insulations, markings, mechanical strengths, ampacity ratings, and uses. These requirements do not apply to conductors that form an integral part of equipment, such as motors, motor controllers, and similar equipment, or to conductors specifically provided for elsewhere in this Code.

Informational Note: For flexible cords and cables, see Article 400. For fixture wires, see Article 402.

310.3 Conductors

(A) Minimum Size of Conductors

The minimum size of conductors for voltage ratings up to and including 2000 volts shall be 14 AWG copper or 12 AWG aluminum or copper-clad aluminum, except as permitted elsewhere in this Code.

(B) Conductor Material

Conductors in this article shall be of aluminum, copper-clad aluminum, or copper unless otherwise specified.

Solid aluminum conductors 8, 10, and 12 AWG shall be made of an AA-8000 series electrical grade aluminum alloy conductor material. Stranded aluminum conductors 8 AWG through 1000 kcmil marked as Type RHH, RHW, XHHW, THW, THHW, THWN, THHN, service-entrance Type SE Style U, and SE Style R shall be made of an AA-8000 series electrical grade aluminum alloy conductor material.

(C) Stranded Conductors

Where installed in raceways, conductors 8 AWG and larger shall be stranded, unless specifically permitted or required elsewhere in this Code to be solid.

(D) Insulated

Conductors not specifically permitted elsewhere in this Code to be covered or bare shall be insulated.

Informational Note: See 250.184 for insulation of neutral conductors of a solidly grounded high-voltage system.

Part II Construction Specifications

310.4 Conductor Constructions and Applications

Insulated conductors shall comply with Table 310.4(A) and Table 310.4(B).

Informational Note: Thermoplastic insulation may stiffen at temperatures lower than —10°C (+14°F). Thermoplastic insulation may also be deformed at normal temperatures where subjected to pressure, such as at points of support.

Table 310.4(A) Conductor Applications and Insulations Rated 600 Volts1

Trade Name Type Letter Maximum

Operating

Temperature Application Provisions Insulation Thickness of Insulation Outer Covering2

AWG or kcmil mm mils

Fluorinated ethylene propylene FEP or FEPB 90°C

(194°F) Dry and damp locations Fluorinated ethylene propylene 14—10 0.51 20 None

8—2 0.76 30

200°C

(392°F) Dry locations — special applications3 Fluorinated ethylene propylene 14—8 0.36 14 Glass braid

6—2 0.36 14 Glass or other suitable braid material

Mineral insulation (metal sheathed) MI 90°C

(194°F) Dry and wet locations Magnesium oxide 18—164 0.58 23 Copper or alloy steel

16—10 0.91 36

250°C

(482°F) For special applications3 9—4 1.27 50

3—500 1.40 55

Moisture-, heat-, and oil-resistant thermoplastic MTW 60°C

(140°F) Machine tool wiring in wet locations Flame-retardant, moisture-, heat-, and oil-resistant thermoplastic (A) (B) (A) (B) (A) None

(B) Nylon jacket or equivalent

90°C

(194°F) Machine tool wiring in dry locations. 22—12 0.76 0.38 30 15

10 0.76 0.51 30 20

8 1.14 0.76 45 30

Informational Note: See NFPA 79. 6 1.52 0.76 60 30

4—2 1.52 1.02 60 40

1—4/0 2.03 1.27 80 50

213—500 2.41 1.52 95 60

501—1000 2.79 1.78 110 70

Paper 85°C

(185°F) For underground service conductors, or by special permission Paper Lead sheath

Perfluoro-alkoxy PFA 90°C

(194°F) Dry and damp locations Perfluoro-alkoxy 14—10 0.51 20 None

8—2 0.76 30

200°C

(392°F) Dry locations — special applications3 1—4/0 1.14 45

Perfluoro-alkoxy PFAH 250°C

(482°F) Dry locations only. Only for leads within apparatus or within raceways connected to apparatus (nickel or nickel-coated copper only) Perfluoro-alkoxy 14—10 0.51 20 None

8—2 0.76 30

1—4/0 1.14 45

Thermoset RHH 90°C

(194°F) Dry and damp locations 14—10 1.14 45 Moisture-resistant, flame-retardant, nonmetallic covering2

8—2 1.52 60

1—4/0 2.03 80

213—500 2.41 95

501—1000 2.79 110

1001—2000 3.18 125

Moisture-resistant thermoset RHW 75°C

(167°F) Dry and wet locations Flame-retardant, moisture-resistant thermoset 14—10 1.14 45 Moisture-resistant, flame-retardant, nonmetallic covering

8—2 1.52 60

1—4/0 2.03 80

RHW-2 90°C

(194°F) 213—500 2.41 95

501—1000 2.79 110

1001—2000 3.18 125

Silicone SA 90°C

(194°F) Dry and damp locations Silicone rubber 14—10 1.14 45 Glass or other suitable braid material

8—2 1.52 60

1—4/0 2.03 80

200°C

(392°F) For special application3 213—500 2.41 95

501—1000 2.79 110

1001—2000 3.18 125

Thermoset SIS 90°C

(194°F) Switchboard and switchgear wiring only Flame-retardant thermoset 14—10 0.76 30 None

8—2 1.14 45

1—4/0 1.40 55

Thermoplastic and fibrous outer braid TBS 90°C

(194°F) Switchboard and switchgear wiring only Thermoplastic 14—10 0.76 30 Flame-retardant, nonmetallic covering

8 1.14 45

6—2 1.52 60

1—4/0 2.03 80

Extended polytetra-fluoro-ethylene TFE 250°C

(482°F) Dry locations only. Only for leads within apparatus or within raceways connected to apparatus, or as open wiring (nickel or nickel-coated copper only) Extruded polytetra-fluoroethylene 14—10 0.51 20 None

8—2 0.76 30

1—4/0 1.14 45

Heat-resistant thermoplastic THHN 90°C

(194°F) Dry and damp locations Flame-retardant, heat-resistant thermoplastic 14—12 0.38 15 Nylon jacket or equivalent

10 0.51 20

8—6 0.76 30

4—2 1.02 40

1—4/0 1.27 50

250—500 1.52 60

501—1000 1.78 70

Moisture- and heat-resistant thermoplastic THHW 75°C

(167°F) Wet location Flame-retardant, moisture- and heat-resistant thermoplastic 14—10 0.76 30 None

8 1.14 45

6—2 1.52 60

90°C

(194°F) Dry location 1—4/0 2.03 80

213—500 2.41 95

501—1000 2.79 110

1001—2000 3.18 125

Moisture- and heat-resistant thermoplastic THW 75°C

(167°F) Dry and wet locations Flame-retardant, moisture- and heat-resistant thermoplastic 14—10 0.76 30 None

8 1.14 45

90°C

(194°F) Special applications within electric discharge lighting equipment. Limited to 1000 open-circuit volts or less. (Size 14—8 only as permitted in 410.68.) 6—2 1.52 60

1—4/0 2.03 80

213—500 2.41 95

501—1000 2.79 110

1001—2000 3.18 125

THW-2 90°C

(194°F) Dry and wet locations

Moisture- and heat-resistant thermoplastic THWN 75°C

(167°F) Dry and wet locations Flame-retardant, moisture- and heat-resistant thermoplastic 14—12 0.38 15 Nylon jacket or equivalent

10 0.51 20

8—6 0.76 30

4—2 1.02 40

THWN-2 90°C

(194°F) 1—4/0 1.27 50

250—500 1.52 60

501—1000 1.78 70

Moisture-resistant thermoplastic TW 60°C

(140°F) Dry and wet locations Flame-retardant, moisture-resistant thermoplastic 14—10 0.76 30 None

8 1.14 45

6—2 1.52 60

1—4/0 2.03 80

213—500 2.41 95

501—1000 2.79 110

1001—2000 3.18 125

Underground feeder and branch-circuit cable — single conductor (for Type UF cable employing more than one conductor, see Article 340). UF 60°C

140°C See Article 340. Moisture-resistant 14—10 1.52 606 Integral with insulation

8—2 2.03 806

75°C

(167°F)5 Moisture- and heat-resistant 1—4/0 2.41 956

Underground service-entrance cable — single conductor (for Type USE cable employing more than one conductor, see Article 338). USE 75°C

(167°F)5 See Article 338. Heat- and moisture-resistant 14—10 1.14 45 Moisture-resistant nonmetallic covering (See 338.2.)

8—2 1.52 60

USE-2 90°C

(194°F) Dry and wet locations 1—4/0 2.03 80

213—500 2.41 957

501—1000 2.79 110

1001—2000 3.18 125

Thermoset XHH 90°C

(194°F) Dry and damp locations Flame-retardant thermoset 14—10 0.76 30 None

8—2 1.14 45

1—4/0 1.40 55

213—500 1.65 65

501—1000 2.03 80

1001—2000 2.41 95

Thermoset XHHN 90°C

(194°F) Dry and damp locations Flame-retardant thermoset 14—12 0.38 15 Nylon jacket or equivalent

10 0.51 20

8—6 0.76 30

4—2 1.02 40

1—4/0 1.27 50

250—500 1.52 60

501—1000 1.78 70

Moisture-resistant thermoset XHHW 90°C

(194°F) Dry and damp locations Flame-retardant, moisture-resistant thermoset 14—10 0.76 30 None

8—2 1.14 45

75°C

(167°F) Wet locations 1—4/0 1.40 55

213—500 1.65 65

501—1000 2.03 80

1001—2000 2.41 95

Moisture-resistant thermoset XHHW-2 90°C

(194°F) Dry and wet locations Flame-retardant, moisture-resistant thermoset 14—10 0.76 30 None

8—2 1.14 45

1—4/0 1.40 55

213—500 1.65 65

501—1000 2.03 80

1001—2000 2.41 95

Moisture-resistant thermoset XHWN 75°C

(167°F) Dry and wet locations Flame-retardant, moisture-resistant thermoset 14—12 0.38 15 Nylon jacket or equivalent

10 0.51 20

8—6 0.76 30

XHWN-2 90°C

(194°F) 4—2 1.02 40

1—4/0 1.27 50

250—500 1.52 60

501—1000 1.78 70

Modified ethylene tetrafluoro-ethylene Z 90°C

(194°F) Dry and damp locations Modified ethylene tetrafluoro-ethylene 14—12 0.38 15 None

10 0.51 20

150°C

(302°F) Dry locations — special applications3 8—4 0.64 25

3—1 0.89 35

1/0—4/0 1.14 45

Modified ethylene tetrafluoro-ethylene ZW 75°C

(167°F) Wet locations Modified ethylene tetrafluoro-ethylene 14—10 0.76 30 None

8—2 1.14 45

90°C

(194°F) Dry and damp locations

150°C

(302°F) Dry locations — special applications3

ZW-2 90°C

(194°F) Dry and wet locations

1Conductors shall be permitted to be rated up to 1000 volts if listed and marked.

2Outer coverings shall not be required where listed without a covering.

3Higher temperature rated constructions shall be permitted where design conditions require maximum conductor operating temperatures above 90°C (194°F).

4Conductor sizes shall be permitted for signaling circuits permitting 300-volt insulation.

5The ampacity of Type UF cable shall be limited in accordance with 340.80.

6Type UF insulation thickness shall include the integral jacket.

7Insulation thickness shall be permitted to be 2.03 mm (80 mils) for listed Type USE conductors that have been subjected to special investigations. The nonmetallic covering over individual rubber-covered conductors of aluminum-sheathed cable and of lead-sheathed or multiconductor cable shall not be required to be flame retardant.

Table 310.104(B) Thickness of Insulation for Nonshielded Types RHH and RHW Solid Dielectric Insulated Conductors Rated 2000 Volts

Conductor Size (AWG or kcmil) Column A1 Column B2

mm mils mm mils

14—10 2.03 80 1.52 60

8 2.03 80 1.78 70

6—2 2.41 95 1.78 70

1—2/0 2.79 110 2.29 90

3/0—4/0 2.79 110 2.29 90

213—500 3.18 125 2.67 105

501—1000 3.56 140 3.05 120

1001—2000 3.56 140 3.56 140

1Column A insulations shall be limited to natural, SBR, and butyl rubbers.

2Column B insulations shall be materials such as cross-linked polyethylene, ethylene propylene rubber, and composites thereof.

310.6 Conductor Identification

(A) Grounded Conductors

Insulated or covered grounded conductors shall be identified in accordance with 200.6.

(B) Equipment Grounding Conductors

Equipment grounding conductors shall be identified in accordance with 250.119.

(C) Ungrounded Conductors

Conductors that are intended for use as ungrounded conductors, whether used as a single conductor or in multiconductor cables, shall be finished to be clearly distinguishable from grounded and equipment grounding conductors. Distinguishing markings shall not conflict in any manner with the surface markings required by 310.8(B)(1). Branch-circuit ungrounded conductors shall be identified in accordance with 210.5(C). Feeders shall be identified in accordance with 215.12.

Exception: Conductor identification shall be permitted in accordance with 200.7.

310.8 Marking

(A) Required Information

All conductors and cables shall be marked to indicate the following information, using the applicable method described in 310.8(B):

The maximum rated voltage.

The proper type letter or letters for the type of wire or cable as specified elsewhere in this Code.

The manufacturer's name, trademark, or other distinctive marking by which the organization responsible for the product can be readily identified.

The AWG size or circular mil area.

Informational Note: See Chapter 9, Table 8, Conductor Properties, for conductor area expressed in SI units for conductor sizes specified in AWG or circular mil area.

Cable assemblies where the neutral conductor is smaller than the ungrounded conductors shall be so marked.

(B) Method of Marking

(1) Surface Marking

The following conductors and cables shall be durably marked on the surface:

Single-conductor and multiconductor thermoset and thermoplastic-insulated wire and cable

Nonmetallic-sheathed cable

Service-entrance cable

Underground feeder and branch-circuit cable

Tray cable

Irrigation cable

Power-limited tray cable

Instrumentation tray cable

The AWG size or circular mil area shall be repeated at intervals not exceeding 610 mm (24 in.). All other markings shall be repeated at intervals not exceeding 1.0 m (40 in.).

(2) Marker Tape

Metal-covered multiconductor cables shall employ a marker tape located within the cable and running for its complete length.

Exception No. 1: Type MI cable shall not require a marker tape.

Exception No. 2: Type AC cable shall not require a marker tape.

Exception No. 3: The information required in 310.8(A) shall be permitted to be durably marked on the outer nonmetallic covering of Type MC, Type ITC, or Type PLTC cables at intervals not exceeding 1.0 m (40 in.).

Exception No. 4: The information required in 310.8(A) shall be permitted to be durably marked on a nonmetallic covering under the metallic sheath of Type ITC or Type PLTC cable at intervals not exceeding 1.0 m (40 in.).

Informational Note: Included in the group of metal-covered cables are Type AC cable (Article 320), Type MC cable (Article 330), and lead-sheathed cable.

(3) Tag Marking

The following conductors and cables shall be marked by means of a printed tag attached to the coil, reel, or carton:

Type MI cable

Switchboard wires

Metal-covered, single-conductor cables

Type AC cable

(4) Optional Marking of Wire Size

The information required in 310.8(A)(4) shall be permitted to be marked on the surface of the individual insulated conductors for the following multiconductor cables:

Type MC cable

Tray cable

Irrigation cable

Power-limited tray cable

Power-limited fire alarm cable

Instrumentation tray cable

(C) Suffixes to Designate Number of Conductors

A type letter or letters used alone shall indicate a single insulated conductor. The letter suffixes shall be indicated as follows:

D — For two insulated conductors laid parallel within an outer nonmetallic covering

M — For an assembly of two or more insulated conductors twisted spirally within an outer nonmetallic covering

(D) Optional Markings

All conductors and cables contained in Chapter 3 shall be permitted to be surface marked to indicate special characteristics of the cable materials. These markings include, but are not limited to, markings for limited smoke, sunlight resistant, and so forth.

Part III Installation

310.10 Uses Permitted

The conductors described in 310.4 shall be permitted for use in any of the wiring methods covered in Chapter 3 and as specified in their respective tables or as permitted elsewhere in this Code.

(A) Dry Locations

Insulated conductors and cables used in dry locations shall be any of the types identified in this Code.

(B) Dry and Damp Locations

Insulated conductors and cables used in dry and damp locations shall be Types FEP, FEPB, MTW, PFA, RHH, RHW, RHW-2, SA, THHN, THW, THW-2, THHW, THWN, THWN-2, TW, XHH, XHHW, XHHW-2, XHHN, XHWN, XHWN-2, Z, or ZW.

(C) Wet Locations

Insulated conductors and cables used in wet locations shall comply with one of the following:

Be moisture-impervious metal-sheathed

Be types MTW, RHW, RHW-2, TW, THW, THW-2, THHW, THWN, THWN-2, XHHW, XHHW-2, XHWN, XHWN-2 or ZW

Be of a type listed for use in wet locations

(D) Locations Exposed to Direct Sunlight

Insulated conductors or cables used where exposed to direct rays of the sun shall comply with (D)(1) or (D)(2):

Conductors and cables shall be listed, or listed and marked, as being sunlight resistant

Conductors and cables shall be covered with insulating material, such as tape or sleeving, that is listed, or listed and marked, as being sunlight resistant

(E) Direct-Burial Conductors

Conductors used for direct-burial applications shall be of a type identified for such use.

(F) Corrosive Conditions

Conductors exposed to oils, greases, vapors, gases, fumes, liquids, or other substances having a deleterious effect on the conductor or insulation shall be of a type suitable for the application.

(G) Conductors in Parallel

(1) General

Aluminum, copper-clad aluminum, or copper conductors for each phase, polarity, neutral, or grounded circuit shall be permitted to be connected in parallel (electrically joined at both ends) only in sizes 1/0 AWG and larger where installed in accordance with 310.10(G)(2) through (G)(6).

Exception No. 1: Conductors in sizes smaller than 1/0 AWG shall be permitted to be run in parallel to supply control power to indicating instruments, contactors, relays, solenoids, and similar control devices, or for frequencies of 360 Hz and higher, provided all of the following apply:

They are contained within the same raceway or cable.

The ampacity of each individual conductor is sufficient to carry the entire load current shared by the parallel conductors.

The overcurrent protection is such that the ampacity of each individual conductor will not be exceeded if one or more of the parallel conductors become inadvertently disconnected.

Exception No. 2: Under engineering supervision, 2 AWG and 1 AWG grounded neutral conductors shall be permitted to be installed in parallel for existing installations.

Informational Note to Exception No. 2: Exception No. 2 can be used to alleviate overheating of neutral conductors in existing installations due to high content of triplen harmonic currents.

(2) Conductor and Installation Characteristics

The paralleled conductors in each phase, polarity, neutral, grounded circuit conductor, equipment grounding conductor, or equipment bonding jumper shall comply with all of the following:

Be the same length

Consist of the same conductor material

Be the same size in circular mil area

Have the same insulation type

Be terminated in the same manner

(3) Separate Cables or Raceways

Where run in separate cables or raceways, the cables or raceways with conductors shall have the same number of conductors and shall have the same electrical characteristics. Conductors of one phase, polarity, neutral, grounded circuit conductor, or equipment grounding conductor shall not be required to have the same physical characteristics as those of another phase, polarity, neutral, grounded circuit conductor, or equipment grounding conductor.

(4) Ampacity Adjustment

Conductors installed in parallel shall comply with the provisions of 310.15(C)(1).

(5) Equipment Grounding Conductors

Where parallel equipment grounding conductors are used, they shall be sized in accordance with 250.122. Sectioned equipment grounding conductors smaller than 1/0 AWG shall be permitted in multiconductor cables, if the combined circular mil area of the sectioned equipment grounding conductors in each cable complies with 250.122.

(6) Bonding Jumpers

Where parallel equipment bonding jumpers or supply-side bonding jumpers are installed in raceways, they shall be sized and installed in accordance with 250.102.

310.12 Single-Phase Dwelling Services and Feeders

For one-family dwellings and the individual dwelling units of two-family and multifamily dwellings, service and feeder conductors supplied by a single-phase, 120/240-volt system shall be permitted to be sized in accordance with 310.12(A) through (D).

For one-family dwellings and the individual dwelling units of two-family and multifamily dwellings, single-phase feeder conductors consisting of two ungrounded conductors and the neutral conductor from a 208Y/120 volt system shall be permitted to be sized in accordance with 310.12(A) through (C).

Table 310.12 Single-Phase Dwelling Services and Feeders

Conductor (AWG or kcmil)

Service or Feeder Rating (Amperes) Copper Aluminum or Copper-Clad Aluminum

100 4 2

110 3 1

125 2 1/0

150 1 2/0

175 1/0 3/0

200 2/0 4/0

225 3/0 250

250 4/0 300

300 250 350

350 350 500

400 400 600

Note: If no adjustment or correction factors are required, this table shall be permitted to be applied.

(A) Services

For a service rated 100 amperes through 400 amperes, the service conductors supplying the entire load associated with a one-family dwelling, or the service conductors supplying the entire load associated with an individual dwelling unit in a two-family or multifamily dwelling, shall be permitted to have an ampacity not less than 83 percent of the service rating. If no adjustment or correction factors are required, Table 310.12 shall be permitted to be applied.

(B) Feeders

For a feeder rated 100 amperes through 400 amperes, the feeder conductors supplying the entire load associated with a one-family dwelling, or the feeder conductors supplying the entire load associated with an individual dwelling unit in a two-family or multifamily dwelling, shall be permitted to have an ampacity not less than 83 percent of the feeder rating. If no adjustment or correction factors are required, Table 310.12 shall be permitted to be applied.

(C) Feeder Ampacities

In no case shall a feeder for an individual dwelling unit be required to have an ampacity greater than that specified in 310.12(A) or (B).

(D) Grounded Conductors

Grounded conductors shall be permitted to be sized smaller than the ungrounded conductors, if the requirements of 220.61 and 230.42 for service conductors or the requirements of 215.2 and 220.61 for feeder conductors are met.

Where correction or adjustment factors are required by 310.15(B) or (C), they shall be permitted to be applied to the ampacity associated with the temperature rating of the conductor.

Informational Note No. 1: The service or feeder ratings addressed by this section are based on the standard ampere ratings for fuses and inverse time circuit breakers from 240.6(A).

Informational Note No. 2: See Example D7 in Annex D.

310.14 Ampacities for Conductors Rated 0 Volts — 2000 Volts

(A) General

(1) Tables or Engineering Supervision

Ampacities for conductors shall be permitted to be determined by tables as provided in 310.15 or under engineering supervision, as provided in 310.14(B).

Informational Note No. 1: Ampacities provided by this section do not take voltage drop into consideration. See 210.19(A), Informational Note No. 4, for branch circuits and 215.2(A), Informational Note No. 2, for feeders.

Informational Note No. 2: For the allowable ampacities of Type MTW wire, see Table 12.5.1 in NFPA 79-2018, Electrical Standard for Industrial Machinery.

(2) Selection of Ampacity

Where more than one ampacity applies for a given circuit length, the lowest value shall be used.

Exception: Where different ampacities apply to portions of a circuit, the higher ampacity shall be permitted to be used if the total portion(s) of the circuit with lower ampacity does not exceed the lesser of 3.0 m (10 ft) or 10 percent of the total circuit.

Informational Note: See 110.14(C) for conductor temperature limitations due to termination provisions.

(3) Temperature Limitation of Conductors

No conductor shall be used in such a manner that its operating temperature exceeds that designated for the type of insulated conductor involved. In no case shall conductors be associated together in such a way, with respect to type of circuit, the wiring method employed, or the number of conductors, that the limiting temperature of any conductor is exceeded.

Informational Note No. 1: The temperature rating of a conductor [see Table 310.4(A) and Table 311.10(A)] is the maximum temperature, at any location along its length, that the conductor can withstand over a prolonged time period without serious degradation. The ampacity tables of Article 310 and the ampacity tables of Informative Annex B, the ambient temperature correction factors in 310.15(B), and the notes to the tables provide guidance for coordinating conductor sizes, types, ampacities, ambient temperatures, and number of associated conductors. The principal determinants of operating temperature are as follows:

Ambient temperature — ambient temperature may vary along the conductor length as well as from time to time.

Heat generated internally in the conductor as the result of load current flow, including fundamental and harmonic currents.

The rate at which generated heat dissipates into the ambient medium. Thermal insulation that covers or surrounds conductors affects the rate of heat dissipation.

Adjacent load-carrying conductors — adjacent conductors have the dual effect of raising the ambient temperature and impeding heat dissipation.

Informational Note No. 2: Refer to 110.14(C) for the temperature limitation of terminations.

(B) Engineering Supervision

Under engineering supervision, conductor ampacities shall be permitted to be calculated by means of Equation 310.14(B).

where:

Tc = conductor temperature in degrees Celsius (°C)

Ta = ambient temperature in degrees Celsius (°C)

Rdc = dc resistance of 305 mm (1 ft) of conductor in microohms at temperature, Tc

Yc = component ac resistance resulting from skin effect and proximity effect

Rca = effective thermal resistance between conductor and surrounding ambient

310.15 Ampacity Tables

(A) General

Ampacities for conductors rated 0 volts to 2000 volts shall be as specified in the Ampacity Table 310.16 through Table 310.21, as modified by 310.15(A) through (F) and 310.12. Under engineering supervision, ampacities of sizes not shown in ampacity tables for conductors meeting the general wiring requirements shall be permitted to be determined by interpolation of the adjacent conductors based on the conductor's area.

The temperature correction and adjustment factors shall be permitted to be applied to the ampacity for the temperature rating of the conductor, if the corrected and adjusted ampacity does not exceed the ampacity for the temperature rating of the termination in accordance with the provisions of 110.14(C).

Informational Note No. 1: Table 310.16 through Table 310.19 are application tables for use in determining conductor sizes on loads calculated in accordance with Part II, Part III, Part IV, or Part V of Article 220. Ampacities result from consideration of one or more of the following:

Temperature compatibility with connected equipment, especially the connection points.

Coordination with circuit and system overcurrent protection.

Compliance with the requirements of product listings or certifications. See 110.3(B).

Preservation of the safety benefits of established industry practices and standardized procedures.

Informational Note No. 2: For conductor area see Chapter 9, Table 8, Conductor Properties. Interpolation is based on the conductor area and not the conductor overall area.

Informational Note No. 3: For the ampacities of flexible cords and cables, see 400.5. For the ampacities of fixture wires, see 402.5.

Informational Note No. 4: For explanation of type letters used in tables and for recognized sizes of conductors for the various conductor insulations, see Table 310.4(A) and Table 310.4(B). For installation requirements, see 310.1 through 310.14 and the various articles of this Code. For flexible cords, see Table 400.4, Table 400.5(A)(1), and Table 400.5(A)(2).

(B) Ambient Temperature Correction Factors

(1) General

Ampacities for ambient temperatures other than those shown in the ampacity tables shall be corrected in accordance with Table 310.15(B)(1) or Table 310.15(B)(2), or shall be permitted to be calculated using Equation 310.15(B).

where:

I' = ampacity corrected for ambient temperature

I = ampacity shown in the tables

Tc = temperature rating of conductor (°C)

Ta' = new ambient temperature (°C)

Ta = ambient temperature used in the table (°C)

Table 310.15(B)(1) Ambient Temperature Correction Factors Based on 30°C (86°F)

For ambient temperatures other than 30°C (86°F), multiply the ampacities specified in the ampacity tables by the appropriate correction factor shown below.

Ambient Temperature (°C) Temperature Rating of Conductor Ambient Temperature (°F)

60°C 75°C 90°C

10 or less 1.29 1.20 1.15 50 or less

11—15 1.22 1.15 1.12 51—59

16—20 1.15 1.11 1.08 60—68

21—25 1.08 1.05 1.04 69—77

26—30 1.00 1.00 1.00 78—86

31—35 0.91 0.94 0.96 87—95

36—40 0.82 0.88 0.91 96—104

41—45 0.71 0.82 0.87 105—113

46—50 0.58 0.75 0.82 114—122

51—55 0.41 0.67 0.76 123—131

56—60 — 0.58 0.71 132—140

61—65 — 0.47 0.65 141—149

66—70 — 0.33 0.58 150—158

71—75 — — 0.50 159—167

76—80 — — 0.41 168—176

81—85 — — 0.29 177—185

(2) Rooftop

For raceways or cables exposed to direct sunlight on or above rooftops where the distance above the roof to the bottom of the raceway or cable is less than 23 mm (7/8 in.), a temperature adder of 33°C (60°F) shall be added to the outdoor temperature to determine the applicable ambient temperature for application of the correction factors in Table 310.15(B)(1) or Table 310.15(B)(2).

Exception: Type XHHW-2 insulated conductors shall not be subject to this ampacity adjustment.

Informational Note: One source for the ambient temperatures in various locations is the ASHRAE Handbook — Fundamentals.

Table 310.15(B)(2) Ambient Temperature Correction Factors Based on 40°C (104°F)

For ambient temperatures other than 40°C (104°F), multiply the ampacities specified in the ampacity tables by the appropriate correction factor shown below.

Ambient Temperature (°C) Temperature Rating of Conductor Ambient Temperature (°F)

60°C 75°C 90°C 150°C 200°C 250°C

10 or less 1.58 1.36 1.26 1.13 1.09 1.07 50 or less

11—15 1.50 1.31 1.22 1.11 1.08 1.06 51—59

16—20 1.41 1.25 1.18 1.09 1.06 1.05 60—68

21—25 1.32 1.2 1.14 1.07 1.05 1.04 69—77

26—30 1.22 1.13 1.10 1.04 1.03 1.02 78—86

31—35 1.12 1.07 1.05 1.02 1.02 1.01 87—95

36—40 1.00 1.00 1.00 1.00 1.00 1.00 96—104

41—45 0.87 0.93 0.95 0.98 0.98 0.99 105—113

46—50 0.71 0.85 0.89 0.95 0.97 0.98 114—122

51—55 0.50 0.76 0.84 0.93 0.95 0.96 123—131

56—60 — 0.65 0.77 0.90 0.94 0.95 132—140

61—65 — 0.53 0.71 0.88 0.92 0.94 141—149

66—70 — 0.38 0.63 0.85 0.90 0.93 150—158

71—75 — — 0.55 0.83 0.88 0.91 159—167

76—80 — — 0.45 0.80 0.87 0.90 168—176

81—90 — — — 0.74 0.83 0.87 177—194

91—100 — — — 0.67 0.79 0.85 195—212

101—110 — — — 0.60 0.75 0.82 213—230

111—120 — — — 0.52 0.71 0.79 231—248

121—130 — — — 0.43 0.66 0.76 249—266

131—140 — — — 0.30 0.61 0.72 267—284

141—160 — — — — 0.50 0.65 285—320

161—180 — — — — 0.35 0.58 321—356

181—200 — — — — — 0.49 357—392

201—225 — — — — — 0.35 393—437

(C) Adjustment Factors

(1) More Than Three Current-Carrying Conductors

The ampacity of each conductor shall be reduced as shown in Table 310.15(C)(1) where the number of current-carrying conductors in a raceway or cable exceeds three, or where single conductors or multiconductor cables not installed in raceways are installed without maintaining spacing for a continuous length longer than 600 mm (24 in.). Each current-carrying conductor of a paralleled set of conductors shall be counted as a current-carrying conductor.

Where conductors of different systems, as provided in 300.3, are installed in a common raceway or cable, the adjustment factors shown in Table 310.15(C)(1) shall apply only to the number of power and lighting conductors (Articles 210, 215, 220, and 230).

Informational Note No. 1: See Annex B for adjustment factors for more than three current-carrying conductors in a raceway or cable with load diversity.

Informational Note No. 2: See 366.23 for adjustment factors for conductors and ampacity for bare copper and aluminum bars in auxiliary gutters and 376.22(B) for adjustment factors for conductors in metal wireways.

(a) Where conductors are installed in cable trays, the provisions of 392.80 shall apply.

(b) Adjustment factors shall not apply to conductors in raceways having a length not exceeding 600 mm (24 in.).

(c) Adjustment factors shall not apply to underground conductors entering or leaving an outdoor trench if those conductors have physical protection in the form of rigid metal conduit, intermediate metal conduit, rigid polyvinyl chloride conduit (PVC), or reinforced thermosetting resin conduit (RTRC) having a length not exceeding 3.05 m (10 ft), and if the number of conductors does not exceed four.

(d) Adjustment factors shall not apply to Type AC cable or to Type MC cable under the following conditions:

The cables do not have an overall outer jacket.

Each cable has not more than three current-carrying conductors.

The conductors are 12 AWG copper.

Not more than 20 current-carrying conductors are installed without maintaining spacing, are stacked, or are supported on "bridle rings."

Exception to (4): If cables meeting the requirements in 310.15(C)(1)(d)(1) through (C)(1)(d)(3) with more than 20 current-carrying conductors are installed longer than 600 mm (24 in.) without maintaining spacing, are stacked, or are supported on bridle rings, a 60 percent adjustment factor shall be applied.

Table 310.15(C)(1) Adjustment Factors for More Than Three Current-Carrying Conductors

Number of Conductors\* Percent of Values in Table 310.16 Through Table 310.19 as Adjusted for Ambient Temperature if Necessary

4—6 80

7—9 70

10—20 50

21—30 45

31—40 40

41 and above 35

\*Number of conductors is the total number of conductors in the raceway or cable, including spare conductors. The count shall be adjusted in accordance with 310.15(E) and (F). The count shall not include conductors that are connected to electrical components that cannot be simultaneously energized.

(2) Raceway Spacing

Spacing between raceways shall be maintained.

(D) Bare or Covered Conductors

Where bare or covered conductors are installed with insulated conductors, the temperature rating of the bare or covered conductor shall be equal to the lowest temperature rating of the insulated conductors for the purpose of determining ampacity.

(E) Neutral Conductor

Neutral conductors shall be considered current carrying in accordance with any of the following:

A neutral conductor that carries only the unbalanced current from other conductors of the same circuit shall not be required to be counted when applying the provisions of 310.15(C)(1).

In a 3-wire circuit consisting of two phase conductors and the neutral conductor of a 4-wire, 3-phase, wye-connected system, a common conductor carries approximately the same current as the line-to-neutral load currents of the other conductors and shall be counted when applying the provisions of 310.15(C)(1).

On a 4-wire, 3-phase wye circuit where the major portion of the load consists of nonlinear loads, harmonic currents are present in the neutral conductor; the neutral conductor shall therefore be considered a current-carrying conductor.

(F) Grounding or Bonding Conductor

A grounding or bonding conductor shall not be counted when applying the provisions of 310.15(C)(1).

310.16 Ampacities of Insulated Conductors in Raceway, Cable, or Earth (Directly Buried)

The ampacities shall be as specified in Table 310.16 where all of the following conditions apply:

Conductors are rated 0 volts through 2000 volts.

Conductors are rated 60°C (140°F), 75°C (167°F), or 90°C (194°F).

Wiring is installed in a 30°C (86°F) ambient temperature.

There are not more than three current-carrying conductors.

Table 310.16 Ampacities of Insulated Conductors with Not More Than Three Current-Carrying Conductors in Raceway, Cable, or Earth (Directly Buried)

Size AWG or kcmil Temperature Rating of Conductor [See Table 310.4(A)] Size AWG or kcmil

60°C (140°F) 75°C (167°F) 90°C (194°F) 60°C (140°F) 75°C (167°F) 90°C (194°F)

Types TW, UF Types RHW, THHW, THW, THWN, XHHW, XHWN, USE, ZW Types TBS, SA, SIS, FEP, FEPB, MI, PFA, RHH, RHW-2, THHN, THHW, THW-2, THWN-2, USE-2, XHH, XHHW, XHHW-2, XHWN, XHWN-2, XHHN, Z, ZW-2 Types TW, UF Types RHW, THHW, THW, THWN, XHHW, XHWN, USE Types TBS, SA, SIS, THHN, THHW, THW-2, THWN-2, RHH, RHW-2, USE-2, XHH, XHHW, XHHW-2, XHWN, XHWN-2, XHHN

COPPER ALUMINUM OR COPPER-CLAD ALUMINUM

18\* — — 14 — — — —

16\* — — 18 — — — —

14\* 15 20 25 — — — —

12\* 20 25 30 15 20 25 12\*

10\* 30 35 40 25 30 35 10\*

8 40 50 55 35 40 45 8

6 55 65 75 40 50 55 6

4 70 85 95 55 65 75 4

3 85 100 115 65 75 85 3

2 95 115 130 75 90 100 2

1 110 130 145 85 100 115 1

1/0 125 150 170 100 120 135 1/0

2/0 145 175 195 115 135 150 2/0

3/0 165 200 225 130 155 175 3/0

4/0 195 230 260 150 180 205 4/0

250 215 255 290 170 205 230 250

300 240 285 320 195 230 260 300

350 260 310 350 210 250 280 350

400 280 335 380 225 270 305 400

500 320 380 430 260 310 350 500

600 350 420 475 285 340 385 600

700 385 460 520 315 375 425 700

750 400 475 535 320 385 435 750

800 410 490 555 330 395 445 800

900 435 520 585 355 425 480 900

1000 455 545 615 375 445 500 1000

1250 495 590 665 405 485 545 1250

1500 525 625 705 435 520 585 1500

1750 545 650 735 455 545 615 1750

2000 555 665 750 470 560 630 2000

Notes:

1. Section 310.15(B) shall be referenced for ampacity correction factors where the ambient temperature is other than 30°C (86°F).

2. Section 310.15(C)(1) shall be referenced for more than three current-carrying conductors.

3. Section 310.16 shall be referenced for conditions of use.

\* Section 240.4(D) shall be referenced for conductor overcurrent protection limitations, except as modified elsewhere in the Code.

310.17 Ampacities of Single-Insulated Conductors in Free Air

The ampacities shall be as specified in Table 310.17 where all of the following conditions apply:

Conductors are rated 0 volts through 2000 volts.

Conductors are rated 60°C (140°F), 75°C (167°F), or 90°C (194°F).

Wiring is installed in a 30°C (86°F) ambient temperature.

Table 310.17 Ampacities of Single-Insulated Conductors in Free Air

Size AWG or kcmil Temperature Rating of Conductor [See Table 310.4(A)] Size AWG or kcmil

60°C (140°F) 75°C (167°F) 90°C (194°F) 60°C (140°F) 75°C (167°F) 90°C (194°F)

Types TW, UF Types RHW, THHW, THW, THWN, XHHW, XHWN, ZW Types TBS, SA, SIS, FEP, FEPB, MI, PFA, RHH, RHW-2, THHN, THHW, THW-2, THWN-2, USE-2, XHH, XHHW, XHHW-2, XHWN, XHWN-2, XHHN, Z, ZW-2 Types TW, UF Types RHW, THHW, THW, THWN, XHHW, XHWN Types TBS, SA, SIS, THHN, THHW, THW-2, THWN-2, RHH, RHW-2, USE-2, XHH, XHHW, XHHW-2, XHWN, XHWN-2, XHHN

COPPER ALUMINUM OR COPPER-CLAD ALUMINUM

18 — — 18 — — — —

16 — — 24 — — — —

14\* 25 30 35 — — — —

12\* 30 35 40 25 30 35 12\*

10\* 40 50 55 35 40 45 10\*

8 60 70 80 45 55 60 8

6 80 95 105 60 75 85 6

4 105 125 140 80 100 115 4

3 120 145 165 95 115 130 3

2 140 170 190 110 135 150 2

1 165 195 220 130 155 175 1

1/0 195 230 260 150 180 205 1/0

2/0 225 265 300 175 210 235 2/0

3/0 260 310 350 200 240 270 3/0

4/0 300 360 405 235 280 315 4/0

250 340 405 455 265 315 355 250

300 375 445 500 290 350 395 300

350 420 505 570 330 395 445 350

400 455 545 615 355 425 480 400

500 515 620 700 405 485 545 500

600 575 690 780 455 545 615 600

700 630 755 850 500 595 670 700

750 655 785 885 515 620 700 750

800 680 815 920 535 645 725 800

900 730 870 980 580 700 790 900

1000 780 935 1055 625 750 845 1000

1250 890 1065 1200 710 855 965 1250

1500 980 1175 1325 795 950 1070 1500

1750 1070 1280 1445 875 1050 1185 1750

2000 1155 1385 1560 960 1150 1295 2000

Notes:

1. Section 310.15(B) shall be referenced for ampacity correction factors where the ambient temperature is other than 30°C (86°F).

2. Section 310.17 shall be referenced for conditions of use.

\* Section 240.4(D) shall be referenced for conductor overcurrent protection limitations, except as modified elsewhere in the Code.

310.18 Ampacities of Insulated Conductors in Raceway or Cable

The ampacities shall be as specified in Table 310.18 where all of the following conditions apply:

Conductors are rated 0 volts through 2000 volts.

Conductors are rated 150°C (302°F), 200°C (392°F), or 250°C (482°F).

Wiring is installed in a 40°C (104°F) ambient temperature.

There are not more than three current-carrying conductors.

Table 310.18 Ampacities of Insulated Conductors with Not More Than Three Current-Carrying Conductors in Raceway or Cable

Size AWG or kcmil Temperature Rating of Conductor [See Table 310.4(A)] Size AWG or kcmil

150°C (302°F) 200°C (392°F) 250°C (482°F) 150°C (302°F)

Type Z Types FEP, FEPB, PFA, SA Types PFAH, TFE Type Z

COPPER NICKEL OR NICKEL-COATED COPPER ALUMINUM OR COPPER-CLAD ALUMINUM

14 34 36 39 — 14

12 43 45 54 30 12

10 55 60 73 44 10

8 76 83 93 57 8

6 96 110 117 75 6

4 120 125 148 94 4

3 143 152 166 109 3

2 160 171 191 124 2

1 186 197 215 145 1

1/0 215 229 244 169 1/0

2/0 251 260 273 198 2/0

3/0 288 297 308 227 3/0

4/0 332 346 361 260 4/0

Notes:

1. Section 310.15(B) shall be referenced for ampacity correction factors where the ambient temperature is other than 40°C (104°F).

2. Section 310.15(C)(1) shall be referenced for more than three current-carrying conductors.

3. Section 310.18 shall be referenced for conditions of use.

310.19 Ampacities of Single-Insulated Conductors in Free Air

The ampacities shall be as specified in Table 310.19 where all of the following conditions apply:

Conductors are rated 0 volts through 2000 volts.

Conductors are rated up to 250°C (482°F).

Wiring is installed in a 40°C (104°F) ambient temperature.

Table 310.19 Ampacities of Single-Insulated Conductors in Free Air

Size AWG or kcmil Temperature Rating of Conductor [See Table 310.4(A)] Size AWG or kcmil

150°C (302°F) 200°C (392°F) 250°C (482°F) 150°C (302°F)

Type Z Types FEP, FEPB, PFA, SA Types PFAH, TFE Type Z

COPPER NICKEL, OR NICKEL-COATED COPPER ALUMINUM OR COPPER-CLAD ALUMINUM

14 46 54 59 — 14

12 60 68 78 47 12

10 80 90 107 63 10

8 106 124 142 83 8

6 155 165 205 112 6

4 190 220 278 148 4

3 214 252 327 170 3

2 255 293 381 198 2

1 293 344 440 228 1

1/0 339 399 532 263 1/0

2/0 390 467 591 305 2/0

3/0 451 546 708 351 3/0

4/0 529 629 830 411 4/0

Notes:

1. Section 310.15(B) shall be referenced for ampacity correction factors where the ambient temperature is other than 40°C (104°F).

2. Section 310.19 shall be referenced for conditions of use.

310.20 Ampacities of Conductors Supported on a Messenger

The ampacities shall be as specified in Table 310.20 where all of the following conditions apply:

Conductors are rated 0 volts through 2000 volts.

Conductors are rated 75°C (167°F) or 90°C (194°F).

Wiring is installed in a 40°C (104°F) ambient temperature.

There are not more than three single-insulated conductors.

Table 310.20 Ampacities of Conductors on a Messenger

Size AWG or kcmil Temperature Rating of Conductor [See Table 310.4(A)] Size AWG or kcmil

75°C (167°F) 90°C (194°F) 75°C (167°F) 90°C (194°F)

Types RHW, THHW, THW, THWN, XHHW, XHWN, ZW Types MI, THHN, THHW, THW-2, THWN-2, RHH, RHW-2, USE-2, XHHW, XHHW-2, XHWN, XHWN-2, ZW-2 Types RHW, THW, THWN, THHW, XHHW, XHWN Types THHN, THHW, RHH, XHHW, RHW-2, XHHW-2, THW-2, THWN-2, XHWN, XHWN-2, USE-2, ZW-2

COPPER ALUMINUM OR COPPER-CLAD ALUMINUM

8 57 66 44 51 8

6 76 89 59 69 6

4 101 117 78 91 4

3 118 138 92 107 3

2 135 158 106 123 2

1 158 185 123 144 1

1/0 183 214 143 167 1/0

2/0 212 247 165 193 2/0

3/0 245 287 192 224 3/0

4/0 287 335 224 262 4/0

250 320 374 251 292 250

300 359 419 282 328 300

350 397 464 312 364 350

400 430 503 339 395 400

500 496 580 392 458 500

600 553 647 440 514 600

700 610 714 488 570 700

750 638 747 512 598 750

800 660 773 532 622 800

900 704 826 572 669 900

1000 748 879 612 716 1000

Notes:

1. Section 310.15(B) shall be referenced for ampacity correction factors where the ambient temperature is other than 40°C (104°F).

2. Section 310.15(C)(1) shall be referenced for more than three current-carrying conductors.

3. Section 310.20 shall be referenced for conditions of use.

310.21 Ampacities of Bare or Covered Conductors in Free Air

The ampacities shall be as specified in Table 310.21 where all of the following conditions apply:

Wind velocity is 610 mm/sec (2 ft/sec).

Conductors are 80°C (176°F) total conductor temperature.

Wiring is installed in a 40°C (104°F) ambient temperature.

Table 310.21 Ampacities Bare or Covered Conductors in Free Air

Copper Conductors AAC Aluminum Conductors

Bare Covered Bare Covered

AWG or kcmil Amperes AWG or kcmil Amperes AWG or kcmil Amperes AWG or kcmil Amperes

8 98 8 103 8 76 8 80

6 124 6 130 6 96 6 101

4 155 4 163 4 121 4 127

2 209 2 219 2 163 2 171

1/0 282 1/0 297 1/0 220 1/0 231

2/0 329 2/0 344 2/0 255 2/0 268

3/0 382 3/0 401 3/0 297 3/0 312

4/0 444 4/0 466 4/0 346 4/0 364

250 494 250 519 266.8 403 266.8 423

300 556 300 584 336.4 468 336.4 492

500 773 500 812 397.5 522 397.5 548

750 1000 750 1050 477.0 588 477.0 617

1000 1193 1000 1253 556.5 650 556.5 682

— — — — 636.0 709 636.0 744

— — — — 795.0 819 795.0 860

— — — — 954.0 920 — —

— — — — 1033.5 968 1033.5 1017

— — — — 1272 1103 1272 1201

— — — — 1590 1267 1590 1381

— — — — 2000 1454 2000 1527

Note: Section 310.21 shall be referenced for conditions of use.

Article 311 Medium Voltage Conductors and Cable

Part I General

311.1 Scope

This article covers the use, installation, construction specifications, and ampacities for Type MV medium voltage conductors and cable.

311.2 Definitions

The definitions in this section shall apply within this article and throughout the Code.

Electrical Ducts. Electrical conduits, or other raceways round in cross section, that are suitable for use underground or embedded in concrete.

Medium Voltage Cable, Type MV. A single or multiconductor solid dielectric insulated cable rated 2001 volts up to and including 35,000 volts, nominal.

Thermal Resistivity. As used in this Code, the heat transfer capability through a substance by conduction.

Informational Note: Thermal resistivity is the reciprocal of thermal conductivity and is designated Rho, which is expressed in the units °C-cm/W.

311.6 Listing Requirements

Type MV cables and associated fittings shall be listed.

Part II Construction Specifications

311.10 Constructions and Applications

Type MV cables shall comply with the applicable provisions in 311.10(A) through (C).

(A) Conductor Application and Insulation

Conductor application and insulation shall comply with Table 311.10(A).

Table 311.10(A) Conductor Application and Insulation Rated 2001 Volts and Higher

Trade Name Type Letter Maximum

Operating

Temperature Application Provision Insulation Outer Covering

Medium voltage solid dielectric MV-90 90°C Dry or wet locations Thermoplastic or

thermosetting Jacket, sheath, or armor

MV-105\* 105°C

\*Where design conditions require maximum conductor temperatures above 90°C.

(B) Thickness of Insulation and Jacket for Nonshielded Insulated Conductors

Thickness of insulation and jacket for nonshielded solid dielectric insulated conductors rated 2001 volts to 5000 volts shall comply with Table 311.10(B).

Table 311.10(B) Thickness of Insulation and Jacket for Nonshielded Solid Dielectric Insulated Conductors Rated 2001 Volts to 5000 Volts

Conductor Size (AWG or kcmil) Dry Locations, Single Conductor Wet or Dry Locations

Without Jacket Insulation With Jacket Single Conductor Multiconductor Insulation\*

Insulation Jacket Insulation Jacket

mm mils mm mils mm mils mm mils mm mils mm mils

8 2.79 110 2.29 90 0.76 30 3.18 125 2.03 80 2.29 90

6 2.79 110 2.29 90 0.76 30 3.18 125 2.03 80 2.29 90

4—2 2.79 110 2.29 90 1.14 45 3.18 125 2.03 80 2.29 90

1—2/0 2.79 110 2.29 90 1.14 45 3.18 125 2.03 80 2.29 90

3/0—4/0 2.79 110 2.29 90 1.65 65 3.18 125 2.41 95 2.29 90

213—500 3.05 120 2.29 90 1.65 65 3.56 140 2.79 110 2.29 90

501—750 3.30 130 2.29 90 1.65 65 3.94 155 3.18 125 2.29 90

751—1000 3.30 130 2.29 90 1.65 65 3.94 155 3.18 125 2.29 90

1001—1250 3.56 140 2.92 115 1.65 65 4.32 170 3.56 140 2.92 115

1251—1500 3.56 140 2.92 115 2.03 80 4.32 170 3.56 140 2.92 115

1501—2000 3.56 140 2.92 115 2.03 80 4.32 170 3.94 155 3.56 140

\*Under a common overall covering such as a jacket, sheath, or armor.

(C) Thickness of Insulation for Shielded Insulated Conductors

Thickness of insulation for shielded solid dielectric insulated conductors rated 2001 volts to 35,000 volts shall comply with Table 311.10(C) and 311.10(C)(1) through (C)(3).

Table 311.10(C) Thickness of Insulation for Shielded Solid Dielectric Insulated Conductors Rated 2001 Volts to 35,000 Volts

Conductor Size (AWG or kcmil) 2001—5000 Volts 5001—8000 Volts 8001—15,000 Volts 15,001—25,000 Volts

100 Percent Insulation Level 100 Percent Insulation Level 133 Percent Insulation Level 173 Percent Insulation Level 100 Percent Insulation Level 133 Percent Insulation Level 173 Percent Insulation Level 100 Percent Insulation Level 133 Percent Insulation Level 173

Percent Insulation Level

mm mils mm mils mm mils mm mils mm mils mm mils mm mils mm mils mm mils mm mils

8 2.29 90 — — — — — — — — — — — — — — — — — —

6—4 2.29 90 2.92 115 3.56 140 4.45 175 — — — — — — — — — — — —

2 2.29 90 2.92 115 3.56 140 4.45 175 445 175 5.59 220 6.60 260 — — — — — —

1 2.29 90 2.92 115 3.56 140 4.45 175 4.45 175 5.59 220 6.60 260 6.60 260 8.13 320 10.67 420

1/0—2000 2.29 90 2.92 115 3.56 140 4.45 175 4.45 175 5.59 220 6.60 260 6.60 260 8.13 320 10.67 420

Conductor Size (AWG or kcmil) 25,001—28,000 Volts 28,001—35,000 Volts

100 Percent Insulation Level 133 Percent Insulation Level 173 Percent Insulation Level 100 Percent Insulation Level 133 Percent Insulation Level 173 Percent Insulation Level

mm mils mm mils mm mils mm mils mm mils mm mils

1 7.11 280 8.76 345 11.30 445 — — — — — —

1/0—2000 7.11 280 8.76 345 11.30 445 8.76 345 10.67 420 14.73 580

(1) 100 Percent Insulation Level

Cables shall be permitted to be applied where the system is provided with relay protection such that ground faults will be cleared as rapidly as possible but, in any case, within 1 minute. These cables are applicable to cable installations that are on grounded systems and shall be permitted to be used on other systems provided the above clearing requirements are met in completely de-energizing the faulted section.

(2) 133 Percent Insulation Level

Cables shall be permitted to be applied in situations where the clearing time requirements of the 100 percent level category cannot be met and the faulted section will be de-energized in a time not exceeding 1 hour. Cable shall be permitted to be used in 100 percent insulation level applications where the installation requires additional insulation.

(3) 173 Percent Insulation Level

Cables shall be permitted to be applied under all of the following conditions:

In industrial establishments where the conditions of maintenance and supervision ensure only qualified persons service the installation

Where the fault clearing time requirements of the 133 percent level category cannot be met

Where an orderly shutdown is required to protect equipment and personnel

Where the faulted section will be de-energized in an orderly shutdown

Cables shall be permitted to be used in 100 percent or 133 percent insulation level applications where the installation requires additional insulation.

311.12 Conductors

(A) Minimum Size of Conductors

The minimum size of conductors shall be as shown in Table 311.12(A), except as permitted elsewhere in this Code.

Table 311.12(A) Minimum Size of Conductors

Conductor Voltage Rating (Volts) Minimum Conductor Size (AWG)

Copper, Aluminum, or Copper-Clad Aluminum

2001—5000 8

5001—8000 6

8001—15,000 2

15,001—28,000 1

28,001—35,000 1/0

(B) Conductor Material

Conductors shall be of aluminum, copper-clad aluminum, or copper unless otherwise specified.

(C) Stranded Conductors

Where installed in raceways, conductors not specifically permitted or required elsewhere in this Code to be solid shall be stranded.

311.14 Conductor Identification

Conductors that are intended for use as ungrounded conductors, whether used as a single conductor or in multiconductor cables, shall be finished to be clearly distinguishable from grounded and grounding conductors. Distinguishing markings shall not conflict in any manner with the surface markings required by 311.16(B)(1). Branch-circuit ungrounded conductors shall be identified in accordance with 210.5(C). Feeders shall be identified in accordance with 215.12.

311.16 Marking

(A) Required Information

All conductors and cables shall be marked to indicate the following information, using the applicable method described in 311.16(B):

The maximum rated voltage

The proper type letter or letters for the type of wire or cable as specified elsewhere in this Code

The manufacturer's name, trademark, or other distinctive marking by which the organization responsible for the product can be readily identified

The AWG size or circular mil area

Informational Note: See Chapter 9, Table 8, Conductor Properties, for conductor area expressed in SI units for conductor sizes specified in AWG or circular mil area.

(B) Method of Marking

One or more of the methods in 311.16(B)(1) through (B)(4) shall be used for marking of cable.

(1) Surface Marking

Cables shall be durably marked on the surface. The AWG size or circular mil area shall be repeated at intervals not exceeding 610 mm (24 in.). All other markings shall be repeated at intervals not exceeding 1.0 m (40 in.).

(2) Marker Tape

Metal-covered multiconductor cables shall employ a marker tape located within the cable and along its complete length.

(3) Tag Marking

Metal-covered, single-conductor cables shall be marked by means of a printed tag attached to the reel.

(4) Optional Marking of Wire Size

The information required in 311.16(A)(4) shall be permitted to be marked on the surface of the individual insulated conductors for multiconductor Type MC cable.

(C) Optional Markings

Cables shall be permitted to be marked to indicate special characteristics of the cable materials, such as limited smoke and sunlight resistance.

Part III Installation

311.30 Installation

Type MV cable shall be installed, terminated, and tested by qualified persons.

Informational Note No. 1: Information about accepted industry practices and installation procedures for medium-voltage cable are described in ANSI/NECA/NCSCB 600, Standard for Installing and Maintaining Medium-Voltage Cable, and in IEEE 576, Recommended Practice for Installation, Termination, and Testing of Insulated Power Cables as Used in Industrial and Commercial Applications.

Informational Note No. 2: Where medium-voltage cable is used for dc circuits, low frequency polarization can create hazardous voltages. When handling the cable these voltages may be present or may develop on dc stressed cable while the circuit is energized. Solidly grounding the cable prior to contacting, cutting or disconnecting cables in dc circuits is a method to discharge these voltages.

311.32 Uses Permitted

Type MV cable shall be permitted for use on power systems rated up to and including 35,000 volts, nominal, as follows:

In wet or dry locations.

In raceways.

In cable trays, where identified for the use, in accordance with 392.10, 392.20(B), (C), and (D), 392.22(C), 392.30(B)(1), 392.46, 392.56, and 392.60. Type MV cable that has an overall metallic sheath or armor, complies with the requirements for Type MC cable, and is identified as "MV or MC" shall be permitted to be installed in cable trays in accordance with 392.10(B)(2).

In messenger-supported wiring in accordance with Part II of Article 396.

As exposed runs in accordance with 300.37. Type MV cable that has an overall metallic sheath or armor, complies with the requirements for Type MC cable, and is identified as "MV or MC" shall be permitted to be installed as exposed runs of metal-clad cable in accordance with 300.37.

Corrosive conditions where exposed to oils, greases, vapors, gases, fumes, liquids, or other substances having a deleterious effect on the conductor or insulation shall be of a type suitable for the application.

Conductors in parallel in accordance with 310.10(G).

Type MV cable used where exposed to direct sunlight shall be identified for the use.

Informational Note: The "uses permitted" is not an all-inclusive list.

311.36 Direct-Burial Conductors

Type MV conductors and cables used for direct burial applications shall be shielded, identified for such use, and installed in accordance with 300.50.

Exception No. 1: Nonshielded multiconductor cables rated 2001 volts to 2400 volts shall be permitted if the cable has an overall metallic sheath or armor.

The metallic shield, sheath, or armor shall be connected to a grounding electrode conductor, a grounding busbar, or a grounding electrode.

Exception No. 2: Airfield lighting cable used in series circuits that are rated up to 5000 volts and are powered by regulators shall be permitted to be nonshielded.

Informational Note to Exception No. 2: Federal Aviation Administration (FAA) Advisory Circulars (ACs) provide additional practices and methods for airport lighting.

311.40 Support

Type MV cable terminated in equipment or installed in pull boxes or vaults shall be secured and supported by metallic or nonmetallic supports suitable to withstand the weight by cable ties listed and identified for securement and support, or other approved means, at intervals not exceeding 1.5 m (5 ft) from terminations or a maximum of 1.8 m (6 ft) between supports.

311.44 Shielding

Nonshielded, ozone-resistant insulated conductors with a maximum phase-to-phase voltage of 5000 volts shall be permitted in Type MC cables in industrial establishments where the conditions of maintenance and supervision ensure that only qualified persons service the installation. For other establishments, solid dielectric insulated conductors operated above 2000 volts in permanent installations shall have ozone-resistant insulation and shall be shielded. All metallic insulation shields shall be connected to a grounding electrode conductor, a grounding busbar, an equipment grounding conductor, or a grounding electrode.

Informational Note: The primary purposes of shielding are to confine the voltage stresses to the insulation, dissipate insulation leakage current, drain off the capacitive charging current, and carry ground-fault current to facilitate operation of ground-fault protective devices in the event of an electrical cable fault.

Exception No. 1: Nonshielded insulated conductors listed by a qualified testing laboratory shall be permitted for use up to 2400 volts under the following conditions:

Conductors shall have insulation resistant to electric discharge and surface tracking, or the insulated conductor(s) shall be covered with a material resistant to ozone, electric discharge, and surface tracking.

Where used in wet locations, the insulated conductor(s) shall have an overall nonmetallic jacket or a continuous metallic sheath.

Insulation and jacket thicknesses shall be in accordance with Table 311.10(B).

Exception No. 2: Nonshielded insulated conductors listed by a qualified testing laboratory shall be permitted for use up to 5000 volts to replace existing nonshielded conductors, on existing equipment in industrial establishments only, under the following conditions:

Where the condition of maintenance and supervision ensures that only qualified personnel install and service the installation.

Conductors shall have insulation resistant to electric discharge and surface tracking, or the insulated conductor(s) shall be covered with a material resistant to ozone, electric discharge, and surface tracking.

Where used in wet locations, the insulated conductor(s) shall have an overall nonmetallic jacket or a continuous metallic sheath.

Insulation and jacket thicknesses shall be in accordance with Table 311.10(B).

Informational Note: Relocation or replacement of equipment may not comply with the term existing as related to this exception.

Exception No. 3: Where permitted in 311.36, Exception No. 2.

Part IV Ampacities

311.60 Ampacities of Conductors

(A) General

(1) Tables or Engineering Supervision

Ampacities for solid dielectric-insulated conductors shall be permitted to be determined by tables or under engineering supervision, as provided in 311.60(B) and (C).

The ampacity of Type MV cable installed in cable tray shall be determined in accordance with 392.80(B).

(2) Selection of Ampacity

Where more than one calculated or tabulated ampacity could apply for a given circuit length, the lowest value shall be used.

Exception: Where different ampacities apply to portions of a circuit, the higher ampacity shall be permitted to be used if the total portion(s) of the circuit with the lower ampacity does not exceed the lesser of 3.0 m (10 ft) or 10 percent of the total circuit.

Informational Note: See 110.40 for conductor temperature limitations due to termination provisions.

(B) Engineering Supervision

Under engineering supervision, conductor ampacities shall be permitted to be calculated by using the following general equation:

where:

Tc = conductor temperature (°C)

Ta = ambient temperature (°C)

ΔTd = dielectric loss temperature rise

Rdc = dc resistance of conductor at temperature, Tc

Yc = component ac resistance resulting from skin effect and proximity effect

Rca = effective thermal resistance between conductor and surrounding ambient

Informational Note: The dielectric loss temperature rise (ΔTd) is negligible for single circuit extruded dielectric cables rated below 46 kilovolts.

(C) Tables

Ampacities for conductors rated 2001 volts to 35,000 volts shall be as specified in Table 311.60(C)(67) through Table 311.60(C)(86). Ampacities for ambient temperatures other than those specified in the ampacity tables shall be corrected in accordance with 311.60(D)(4).

Informational Note No. 1: For ampacities calculated in accordance with 311.60(A), reference IEEE 835, Standard Power Cable Ampacity Tables, and the references therein for availability of all factors and constants.

Informational Note No. 2: Ampacities provided by this section do not take voltage drop into consideration. See 210.19(A), Informational Note No. 4, for branch circuits and 215.2(A), Informational Note No. 2, for feeders.

Table 311.60(C)(67) Ampacities of Insulated Single Copper Conductor Cables Triplexed in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 65 74 — —

6 90 99 100 110

4 120 130 130 140

2 160 175 170 195

1 185 205 195 225

1/0 215 240 225 255

2/0 250 275 260 295

3/0 290 320 300 340

4/0 335 375 345 390

250 375 415 380 430

350 465 515 470 525

500 580 645 580 650

750 750 835 730 820

1000 880 980 850 950

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(68) Ampacities of Insulated Single Aluminum Conductor Cables Triplexed in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 50 57 — —

6 70 77 75 84

4 90 100 100 110

2 125 135 130 150

1 145 160 150 175

1/0 170 185 175 200

2/0 195 215 200 230

3/0 225 250 230 265

4/0 265 290 270 305

250 295 325 300 335

350 365 405 370 415

500 460 510 460 515

750 600 665 590 660

1000 715 800 700 780

Note: Refer to 311.60(E) for basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(69) Ampacities of Insulated Single Copper Conductor Isolated in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—15,000 Volts Ampacity 15,001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 83 93 — — — —

6 110 120 110 125 — —

4 145 160 150 165 — —

2 190 215 195 215 — —

1 225 250 225 250 225 250

1/0 260 290 260 290 260 290

2/0 300 330 300 335 300 330

3/0 345 385 345 385 345 380

4/0 400 445 400 445 395 445

250 445 495 445 495 440 490

350 550 615 550 610 545 605

500 695 775 685 765 680 755

750 900 1000 885 990 870 970

1000 1075 1200 1060 1185 1040 1160

1250 1230 1370 1210 1350 1185 1320

1500 1365 1525 1345 1500 1315 1465

1750 1495 1665 1470 1640 1430 1595

2000 1605 1790 1575 1755 1535 1710

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(70) Ampacities of Insulated Single Aluminum Conductor Isolated in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—15,000 Volts Ampacity 15,001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 64 71 — — — —

6 85 95 87 97 — —

4 115 125 115 130 — —

2 150 165 150 170 — —

1 175 195 175 195 175 195

1/0 200 225 200 225 200 225

2/0 230 260 235 260 230 260

3/0 270 300 270 300 270 300

4/0 310 350 310 350 310 345

250 345 385 345 385 345 380

350 430 480 430 480 430 475

500 545 605 535 600 530 590

750 710 790 700 780 685 765

1000 855 950 840 940 825 920

1250 980 1095 970 1080 950 1055

1500 1105 1230 1085 1215 1060 1180

1750 1215 1355 1195 1335 1165 1300

2000 1320 1475 1295 1445 1265 1410

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(71) Ampacities of an Insulated Three-Conductor Copper Cable Isolated in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 59 66 — —

6 79 88 93 105

4 105 115 120 135

2 140 154 165 185

1 160 180 185 210

1/0 185 205 215 240

2/0 215 240 245 275

3/0 250 280 285 315

4/0 285 320 325 360

250 320 355 360 400

350 395 440 435 490

500 485 545 535 600

750 615 685 670 745

1000 705 790 770 860

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(72) Ampacities of an Insulated Three-Conductor Aluminum Cable Isolated in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 46 51 — —

6 61 68 72 80

4 81 90 95 105

2 110 120 125 145

1 125 140 145 165

1/0 145 160 170 185

2/0 170 185 190 215

3/0 195 215 220 245

4/0 225 250 255 285

250 250 280 280 315

350 310 345 345 385

500 385 430 425 475

750 495 550 540 600

1000 585 650 635 705

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(73) Ampacities of an Insulated Triplexed or Three Single-Conductor Copper Cables in Isolated Conduit in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 55 61 — —

6 75 84 83 93

4 97 110 110 120

2 130 145 150 165

1 155 175 170 190

1/0 180 200 195 215

2/0 205 225 225 255

3/0 240 270 260 290

4/0 280 305 295 330

250 315 355 330 365

350 385 430 395 440

500 475 530 480 535

750 600 665 585 655

1000 690 770 675 755

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(74) Ampacities of an Insulated Triplexed or Three Single-Conductor Aluminum Cables in Isolated Conduit in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 43 48 — —

6 58 65 65 72

4 76 85 84 94

2 100 115 115 130

1 120 135 130 150

1/0 140 155 150 170

2/0 160 175 175 200

3/0 190 210 200 225

4/0 215 240 230 260

250 250 280 255 290

350 305 340 310 350

500 380 425 385 430

750 490 545 485 540

1000 580 645 565 640

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(75) Ampacities of an Insulated Three-Conductor Copper Cable in Isolated Conduit in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 52 58 — —

6 69 77 83 92

4 91 100 105 120

2 125 135 145 165

1 140 155 165 185

1/0 165 185 195 215

2/0 190 210 220 245

3/0 220 245 250 280

4/0 255 285 290 320

250 280 315 315 350

350 350 390 385 430

500 425 475 470 525

750 525 585 570 635

1000 590 660 650 725

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(76) Ampacities of an Insulated Three-Conductor Aluminum Cable in Isolated Conduit in Air

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

8 41 46 — —

6 53 59 64 71

4 71 79 84 94

2 96 105 115 125

1 110 125 130 145

1/0 130 145 150 170

2/0 150 165 170 190

3/0 170 190 195 220

4/0 200 225 225 255

250 220 245 250 280

350 275 305 305 340

500 340 380 380 425

750 430 480 470 520

1000 505 560 550 615

Note: Refer to 311.60(E) for the basis of ampacities, 311.10(A) for conductor maximum operating temperature and application, and 311.60(D)(4) for the ampacity correction factors where the ambient air temperature is other than 40°C (104°F).

Table 311.60(C)(77) Ampacities of Three Single-Insulated Copper Conductors in Underground Electrical Ducts (Three Conductors per Electrical Duct)

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit [See Figure 311.60(D)(3), Detail 1.]

8 64 69 — —

6 85 92 90 97

4 110 120 115 125

2 145 155 155 165

1 170 180 175 185

1/0 195 210 200 215

2/0 220 235 230 245

3/0 250 270 260 275

4/0 290 310 295 315

250 320 345 325 345

350 385 415 390 415

500 470 505 465 500

750 585 630 565 610

1000 670 720 640 690

Three Circuits [See Figure 311.60(D)(3), Detail 2.]

8 56 60 — —

6 73 79 77 83

4 95 100 99 105

2 125 130 130 135

1 140 150 145 155

1/0 160 175 165 175

2/0 185 195 185 200

3/0 210 225 210 225

4/0 235 255 240 255

250 260 280 260 280

350 315 335 310 330

500 375 405 370 395

750 460 495 440 475

1000 525 565 495 535

Six Circuits [See Figure 311.60(D)(3), Detail 3.]

8 48 52 — —

6 62 67 64 68

4 80 86 82 88

2 105 110 105 115

1 115 125 120 125

1/0 135 145 135 145

2/0 150 160 150 165

3/0 170 185 170 185

4/0 195 210 190 205

250 210 225 210 225

350 250 270 245 265

500 300 325 290 310

750 365 395 350 375

1000 410 445 390 415

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(78) Ampacities of Three Single-Insulated Aluminum Conductors in Underground Electrical Ducts (Three Conductors per Electrical Duct)

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit [See Figure 311.60(D)(3), Detail 1.]

8 50 54 — —

6 66 71 70 75

4 86 93 91 98

2 115 125 120 130

1 130 140 135 145

1/0 150 160 155 165

2/0 170 185 175 190

3/0 195 210 200 215

4/0 225 245 230 245

250 250 270 250 270

350 305 325 305 330

500 370 400 370 400

750 470 505 455 490

1000 545 590 525 565

Three Circuits [See Figure 311.60(D)(3), Detail 2.]

8 44 47 — —

6 57 61 60 65

4 74 80 77 83

2 96 105 100 105

1 110 120 110 120

1/0 125 135 125 140

2/0 145 155 145 155

3/0 160 175 165 175

4/0 185 200 185 200

250 205 220 200 220

350 245 265 245 260

500 295 320 290 315

750 370 395 355 385

1000 425 460 405 440

Six Circuits [See Figure 311.60(D)(3), Detail 3.]

8 38 41 — —

6 48 52 50 54

4 62 67 64 69

2 80 86 80 88

1 91 98 90 99

1/0 105 110 105 110

2/0 115 125 115 125

3/0 135 145 130 145

4/0 150 165 150 160

250 165 180 165 175

350 195 210 195 210

500 240 255 230 250

750 290 315 280 305

1000 335 360 320 345

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(79) Ampacities of Three Insulated Copper Conductors Cabled Within an Overall Covering (Three-Conductor Cable) in Underground Electrical Ducts (One Cable per Electrical Duct)

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit [See Figure 311.60(D)(3), Detail 1.]

8 59 64 — —

6 78 84 88 95

4 100 110 115 125

2 135 145 150 160

1 155 165 170 185

1/0 175 190 195 210

2/0 200 220 220 235

3/0 230 250 250 270

4/0 265 285 285 305

250 290 315 310 335

350 355 380 375 400

500 430 460 450 485

750 530 570 545 585

1000 600 645 615 660

Three Circuits [See Figure 311.60(D)(3), Detail 2.]

8 53 57 — —

6 69 74 75 81

4 89 96 97 105

2 115 125 125 135

1 135 145 140 155

1/0 150 165 160 175

2/0 170 185 185 195

3/0 195 210 205 220

4/0 225 240 230 250

250 245 265 255 270

350 295 315 305 325

500 355 380 360 385

750 430 465 430 465

1000 485 520 485 515

Six Circuits [See Figure 311.60(D)(3), Detail 3.]

8 46 50 — —

6 60 65 63 68

4 77 83 81 87

2 98 105 105 110

1 110 120 115 125

1/0 125 135 130 145

2/0 145 155 150 160

3/0 165 175 170 180

4/0 185 200 190 200

250 200 220 205 220

350 240 270 245 275

500 290 310 290 305

750 350 375 340 365

1000 390 420 380 405

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(80) Ampacities of Three Insulated Aluminum Conductors Cabled Within an Overall Covering (Three-Conductor Cable) in Underground Electrical Ducts (One Cable per Electrical Duct)

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit [See Figure 311.60(D)(3), Detail 1.]

8 46 50 — —

6 61 66 69 74

4 80 86 89 96

2 105 110 115 125

1 120 130 135 145

1/0 140 150 150 165

2/0 160 170 170 185

3/0 180 195 195 210

4/0 205 220 220 240

250 230 245 245 265

350 280 310 295 315

500 340 365 355 385

750 425 460 440 475

1000 495 535 510 545

Three Circuits [See Figure 311.60(D)(3), Detail 2.]

8 41 44 — —

6 54 58 59 64

4 70 75 75 81

2 90 97 100 105

1 105 110 110 120

1/0 120 125 125 135

2/0 135 145 140 155

3/0 155 165 160 175

4/0 175 185 180 195

250 190 205 200 215

350 230 250 240 255

500 280 300 285 305

750 345 375 350 375

1000 400 430 400 430

Six Circuits [See Figure 311.60(D)(3), Detail 3.]

8 36 39 — —

6 46 50 49 53

4 60 65 63 68

2 77 83 80 86

1 87 94 90 98

1/0 99 105 105 110

2/0 110 120 115 125

3/0 130 140 130 140

4/0 145 155 150 160

250 160 170 160 170

350 190 205 190 205

500 230 245 230 245

750 280 305 275 295

1000 320 345 315 335

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(81) Ampacities of Single Insulated Copper Conductors Directly Buried in Earth

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit, Three Conductors [See Figure 311.60(D)(3), Detail 9.]

8 110 115 — —

6 140 150 130 140

4 180 195 170 180

2 230 250 210 225

1 260 280 240 260

1/0 295 320 275 295

2/0 335 365 310 335

3/0 385 415 355 380

4/0 435 465 405 435

250 470 510 440 475

350 570 615 535 575

500 690 745 650 700

750 845 910 805 865

1000 980 1055 930 1005

Two Circuits, Six Conductors [See Figure 311.60(D)(3), Detail 10.]

8 100 110 — —

6 130 140 120 130

4 165 180 160 170

2 215 230 195 210

1 240 260 225 240

1/0 275 295 255 275

2/0 310 335 290 315

3/0 355 380 330 355

4/0 400 430 375 405

250 435 470 410 440

350 520 560 495 530

500 630 680 600 645

750 775 835 740 795

1000 890 960 855 920

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(82) Ampacities of Single Insulated Aluminum Conductors Directly Buried in Earth

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit, Three Conductors [See Figure 311.60(D)(3), Detail 9.]

8 85 90 — —

6 110 115 100 110

4 140 150 130 140

2 180 195 165 175

1 205 220 185 200

1/0 230 250 215 230

2/0 265 285 245 260

3/0 300 320 275 295

4/0 340 365 315 340

250 370 395 345 370

350 445 480 415 450

500 540 580 510 545

750 665 720 635 680

1000 780 840 740 795

Two Circuits, Six Conductors [See Figure 311.60(D)(3), Detail 10.]

8 80 85 — —

6 100 110 95 100

4 130 140 125 130

2 165 180 155 165

1 190 200 175 190

1/0 215 230 200 215

2/0 245 260 225 245

3/0 275 295 255 275

4/0 310 335 290 315

250 340 365 320 345

350 410 440 385 415

500 495 530 470 505

750 610 655 580 625

1000 710 765 680 730

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(83) Ampacities of Three Insulated Copper Conductors Cabled Within an Overall Covering (Three-Conductor Cable), Directly Buried in Earth

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit [See Figure 311.60(D)(3), Detail 5.]

8 85 89 — —

6 105 115 115 120

4 135 150 145 155

2 180 190 185 200

1 200 215 210 225

1/0 230 245 240 255

2/0 260 280 270 290

3/0 295 320 305 330

4/0 335 360 350 375

250 365 395 380 410

350 440 475 460 495

500 530 570 550 590

750 650 700 665 720

1000 730 785 750 810

Two Circuits [See Figure 311.60(D)(3), Detail 6.]

8 80 84 — —

6 100 105 105 115

4 130 140 135 145

2 165 180 170 185

1 185 200 195 210

1/0 215 230 220 235

2/0 240 260 250 270

3/0 275 295 280 305

4/0 310 335 320 345

250 340 365 350 375

350 410 440 420 450

500 490 525 500 535

750 595 640 605 650

1000 665 715 675 730

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(84) Ampacities of Three Insulated Aluminum Conductors Cabled Within an Overall Covering (Three-Conductor Cable), Directly Buried in Earth

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit [See Figure 311.60(D)(3), Detail 5.]

8 65 70 — —

6 80 88 90 95

4 105 115 115 125

2 140 150 145 155

1 155 170 165 175

1/0 180 190 185 200

2/0 205 220 210 225

3/0 230 250 240 260

4/0 260 280 270 295

250 285 310 300 320

350 345 375 360 390

500 420 450 435 470

750 520 560 540 580

1000 600 650 620 665

Two Circuits [See Figure 311.60(D)(3), Detail 6.]

8 60 66 — —

6 75 83 80 95

4 100 110 105 115

2 130 140 135 145

1 145 155 150 165

1/0 165 180 170 185

2/0 190 205 195 210

3/0 215 230 220 240

4/0 245 260 250 270

250 265 285 275 295

350 320 345 330 355

500 385 415 395 425

750 480 515 485 525

1000 550 590 560 600

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(85) Ampacities of Three Triplexed Single Insulated Copper Conductors Directly Buried in Earth

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit, Three Conductors [See Figure 311.60(D)(3), Detail 7.]

8 90 95 — —

6 120 130 115 120

4 150 165 150 160

2 195 205 190 205

1 225 240 215 230

1/0 255 270 245 260

2/0 290 310 275 295

3/0 330 360 315 340

4/0 375 405 360 385

250 410 445 390 410

350 490 580 470 505

500 590 635 565 605

750 725 780 685 740

1000 825 885 770 830

Two Circuits, Six Conductors [See Figure 311.60(D)(3), Detail 8.]

8 85 90 — —

6 110 115 105 115

4 140 150 140 150

2 180 195 175 190

1 205 220 200 215

1/0 235 250 225 240

2/0 265 285 255 275

3/0 300 320 290 315

4/0 340 365 325 350

250 370 395 355 380

350 445 480 425 455

500 535 575 510 545

750 650 700 615 660

1000 740 795 690 745

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

Table 311.60(C)(86) Ampacities of Three Triplexed Single Insulated Aluminum Conductors Directly Buried in Earth

Conductor Size (AWG or kcmil) Temperature Rating of Conductor

2001—5000 Volts Ampacity 5001—35,000 Volts Ampacity

90°C (194°F) Type MV-90 105°C (221°F) Type MV-105 90°C (194°F) Type MV-90 105°C (221°F) Type MV-105

One Circuit, Three Conductors [See Figure 311.60(D)(3), Detail 7.]

8 70 75 — —

6 90 100 90 95

4 120 130 115 125

2 155 165 145 155

1 175 190 165 175

1/0 200 210 190 205

2/0 225 240 215 230

3/0 255 275 245 265

4/0 290 310 280 305

250 320 350 305 325

350 385 420 370 400

500 465 500 445 480

750 580 625 550 590

1000 670 725 635 680

Two Circuits, Six Conductors [See Figure 311.60(D)(3), Detail 8.]

8 65 70 — —

6 85 95 85 90

4 110 120 105 115

2 140 150 135 145

1 160 170 155 170

1/0 180 195 175 190

2/0 205 220 200 215

3/0 235 250 225 245

4/0 265 285 255 275

250 290 310 280 300

350 350 375 335 360

500 420 455 405 435

750 520 560 485 525

1000 600 645 565 605

Note: Refer to 311.60(F) for basis of ampacities and Table 311.10(A) for the temperature rating of the conductor.

(D) Ampacity Adjustment

(1) Grounded Shields

Ampacities shown in Table 311.60(C)(69), Table 311.60(C)(70), Table 311.60(C)(81), and Table 311.60(C)(82) shall apply for cables with shields grounded at one point only. Where shields for these cables are grounded at more than one point, ampacities shall be adjusted to take into consideration the heating due to shield currents.

Informational Note: Tables other than those listed contain the ampacity of cables with shields grounded at multiple points.

(2) Burial Depth

Where the burial depth of direct burial or electrical duct bank circuits is modified from the values shown in a figure or table, ampacities shall be permitted to be modified as indicated in 311.60(D)(2)(a) and (D)(2)(b). No ampacity adjustments shall be required where the burial depth is decreased.

(a) Where burial depths are increased in part(s) of an electrical duct run, a decrease in ampacity of the conductors shall not be required, provided the total length of parts of the duct run increased in depth is less than 25 percent of the total run length.

(b) Where burial depths are deeper than shown in a specific underground ampacity table or figure, an ampacity derating factor of 6 percent per 300 mm (1 ft) increase in depth for all values of rho shall be permitted.

(3) Electrical Ducts Entering Equipment Enclosures

At locations where electrical ducts enter equipment enclosures from underground, spacing between such ducts, as shown in Figure 311.60(D)(3), shall be permitted to be reduced without requiring the ampacity of conductors therein to be reduced.

FIGURE 311.60(D)(3) Cable Installation Dimensions for Use with Table 311.60(C)(77) Through Table 311.60(C)(86).

(4) Ambient Temperature Correction

Ampacities for ambient temperatures other than those specified in the ampacity tables shall be corrected in accordance with Table 311.60(D)(4) or shall be permitted to be calculated using the following equation:

where:

I' = ampacity corrected for ambient temperature

I = ampacity shown in the table for Tc and Ta

Tc = temperature rating of conductor (°C)

Ta' = new ambient temperature (°C)

Ta = ambient temperature used in the table (°C)

Table 311.60(D)(4) Ambient Temperature Correction Factors

For ambient temperatures other than 40°C (104°F), multiply the allowable ampacities specified in the ampacity tables by the appropriate factor shown below.

Ambient Temperature (°C) Temperature Rating of Conductor Ambient Temperature (°F)

90°C 105°C

10 or less 1.26 1.21 50 or less

11—15 1.22 1.18 51—59

16—20 1.18 1.14 60—68

21—25 1.14 1.11 69—77

26—30 1.10 1.07 78—86

31—35 1.05 1.04 87—95

36—40 1.00 1.00 96—104

41—45 0.95 0.96 105—113

46—50 0.89 0.92 114—122

51—55 0.84 0.88 123—131

56—60 0.77 0.83 132—140

61—65 0.71 0.78 141—149

66—70 0.63 0.73 150—158

71—75 0.55 0.68 159—167

76—80 0.45 0.62 168—176

81—85 0.32 0.55 177—185

86—90 — 0.48 186—194

91—95 — 0.39 195—203

96—100 — 0.28 204—212

(E) Ampacity in Air

Ampacities for conductors and cables in air shall be as specified in Table 311.60(C)(67) through Table 311.60(C)(76). Ampacities shall be based on the following:

Conductor temperatures of 90°C (194°F) and 105°C (221°F)

Ambient air temperature of 40°C (104°F)

Informational Note: See 311.60(D)(4) where the ambient air temperature is other than 40°C (104°F).

(F) Ampacity in Underground Electrical Ducts and Direct Buried in Earth

Ampacities for conductors and cables in underground electrical ducts and direct buried in earth shall be as specified in Table 311.60(C)(77) through Table 311.60(C)(86). Ampacities shall be based on the following:

Ambient earth temperature of 20°C (68°F)

Arrangement in accordance with Figure 311.60(D)(3)

100 percent load factor

Thermal resistance (Rho) of 90

Conductor temperatures 90°C (194°F) and 105°C (221°F)

Minimum burial depths to the top electrical ducts or cables shall be in accordance with 300.50.

Maximum depth to the top of electrical duct banks shall be 750 mm (30 in.), and maximum depth to the top of direct-buried cables shall be 900 mm (36 in.).

Article 312 Cabinets, Cutout Boxes, and Meter Socket Enclosures

Part I Scope and Installation

312.1 Scope

This article covers the installation and construction specifications of cabinets, cutout boxes, and meter socket enclosures. It does not apply to equipment operating at over 1000 volts, except as specifically referenced elsewhere in the Code.

312.2 Damp and Wet Locations

In damp or wet locations, surface-type enclosures within the scope of this article shall be placed or equipped so as to prevent moisture or water from entering and accumulating within the cabinet or cutout box, and shall be mounted so there is at least 6-mm (1/4-in.) airspace between the enclosure and the wall or other supporting surface. Enclosures installed in wet locations shall be weatherproof. For enclosures in wet locations, raceways or cables entering above the level of uninsulated live parts shall use fittings listed for wet locations.

Exception: Nonmetallic enclosures shall be permitted to be installed without the airspace on a concrete, masonry, tile, or similar surface.

Informational Note: For protection against corrosion, see 300.6.

312.3 Position in Wall

In walls of concrete, tile, or other noncombustible material, cabinets shall be installed so that the front edge of the cabinet is not set back of the finished surface more than 6 mm (1/4 in.). In walls constructed of wood or other combustible material, cabinets shall be flush with the finished surface or project therefrom.

312.4 Repairing Noncombustible Surfaces

Noncombustible surfaces that are broken or incomplete shall be repaired so there will be no gaps or open spaces greater than 3 mm (1/8 in.) at the edge of the cabinet or cutout box employing a flush-type cover.

312.5 Cabinets, Cutout Boxes, and Meter Socket Enclosures

Conductors entering enclosures within the scope of this article shall be protected from abrasion and shall comply with 312.5(A) through (C).

(A) Openings to Be Closed

Openings through which conductors enter shall be closed in an approved manner.

(B) Metal Cabinets, Cutout Boxes, and Meter Socket Enclosures

Where metal enclosures within the scope of this article are installed with messenger-supported wiring, open wiring on insulators, or concealed knob-and-tube wiring, conductors shall enter through insulating bushings or, in dry locations, through flexible tubing extending from the last insulating support and firmly secured to the enclosure.

(C) Cables

Where cable is used, each cable shall be secured to the cabinet, cutout box, or meter socket enclosure.

Exception No. 1: Cables with entirely nonmetallic sheaths shall be permitted to enter the top of a surface-mounted enclosure through one or more nonflexible raceways not less than 450 mm (18 in.) and not more than 3.0 m (10 ft) in length, provided all of the following conditions are met:

Each cable is fastened within 300 mm (12 in.), measured along the sheath, of the outer end of the raceway.

The raceway extends directly above the enclosure and does not penetrate a structural ceiling.

A fitting is provided on each end of the raceway to protect the cable(s) from abrasion and the fittings remain accessible after installation.

The raceway is sealed or plugged at the outer end using approved means so as to prevent access to the enclosure through the raceway.

The cable sheath is continuous through the raceway and extends into the enclosure beyond the fitting not less than 6 mm (1/4 in.).

The raceway is fastened at its outer end and at other points in accordance with the applicable article.

Where installed as conduit or tubing, the cable fill does not exceed the amount that would be permitted for complete conduit or tubing systems by Table 1 of Chapter 9 of this Code and all applicable notes thereto. Note 2 to the tables in Chapter 9 does not apply to this condition.

Informational Note: See Table 1 in Chapter 9, including Note 9, for allowable cable fill in circular raceways. See 310.15(C)(1) for required ampacity reductions for multiple cables installed in a common raceway.

Exception No. 2: Single conductors and multiconductor cables shall be permitted to enter enclosures in accordance with 392.46(A) or (B).

312.6 Deflection of Conductors

Conductors at terminals or conductors entering or leaving cabinets, cutout boxes, and meter socket enclosures shall comply with 312.6(A) through (C).

Exception: Wire-bending space in enclosures for motor controllers with provisions for one or two wires per terminal shall comply with 430.10(B).

(A) Width of Wiring Gutters

Conductors shall not be deflected within a cabinet or cutout box unless a gutter having a width in accordance with Table 312.6(A) is provided. Conductors in parallel in accordance with 310.10(G) shall be judged on the basis of the number of conductors in parallel.

Table 312.6(A) Minimum Wire-Bending Space at Terminals and Minimum Width of Wiring Gutters

Wire Size (AWG or kcmil) Wires per Terminal

All Other Conductors Compact Stranded AA-8000 Aluminum Alloy Conductors (see Note 2) 1 2 3 4 5

mm in. mm in. mm in. mm in. mm in.

14—10 12—8 Not specified — — — — — — — —

8—6 6—4 38.1 11/2 — — — — — — — —

4—3 2—1 50.8 2 — — — — — — — —

2 1/0 63.5 21/2 — — — — — — — —

1 2/0 76.2 3 — — — — — — — —

1/0—2/0 3/0—4/0 88.9 31/2 127 5 178 7 — — — —

3/0—4/0 250—300 102 4 152 6 203 8 — — — —

250 350 114 41/2 152 6 203 8 254 10 — —

300—350 400—500 127 5 203 8 254 10 305 12 — —

400—500 600—750 152 6 203 8 254 10 305 12 356 14

600—700 800—1000 203 8 254 10 305 12 356 14 406 16

750—900 — 203 8 305 12 356 14 406 16 457 18

1000—1250 — 254 10 — — — — — — — —

1500—2000 — 305 12 — — — — — — — —

Notes:

1. Bending space at terminals shall be measured in a straight line from the end of the lug or wire connector (in the direction that the wire leaves the terminal) to the wall, barrier, or obstruction.

2. This column shall be permitted to be used to determine the minimum wire-bending space for compact stranded aluminum conductors in sizes up to 1000 kcmil and manufactured using AA-8000 series electrical grade aluminum alloy conductor material in accordance with 310.3(B). The minimum width of the wire gutter space shall be determined using the all other conductors value in this table.

(B) Wire-Bending Space at Terminals

Wire-bending space at each terminal shall be provided in accordance with 312.6(B)(1) or (B)(2).

Table 312.6(B) Minimum Wire-Bending Space at Terminals

Wire Size (AWG or kcmil) Wires per Terminal

1 2 3 4 or More

All Other Conductors Compact Stranded AA-8000 Aluminum Alloy Conductors (See Note 3.) mm in. mm in. mm in. mm in.

14—10 12—8 Not specified — — — — —

8 6 38.1 11/2 — — — — —

6 4 50.8 2 — — — — —

4 2 76.2 3 — — — — —

3 1 76.2 3 — — — — —

2 1/0 88.9 31/2 — — — — —

1 2/0 114 41/2 — — — — —

1/0 3/0 140 51/2 140 51/2 178 7 — —

2/0 4/0 152 6 152 6 190 71/2 — —

3/0 250 165a 61/2a 165a 61/2a 203 8 — —

4/0 300 178b 7b 190c 71/2c 216a 81/2a — —

250 350 216d 81/2d 216d 81/2d 229b 9b 254 10

300 400 254e 10e 254d 10d 279b 11b 305 12

350 500 305e 12e 305e 12e 330e 13e 356d 14d

400 600 330e 13e 330e 13e 356e 14e 381e 15e

500 700—750 356e 14e 356e 14e 381e 15e 406e 16e

600 800—900 381e 15e 406e 16e 457e 18e 483e 19e

700 1000 406e 16e 457e 18e 508e 20e 559e 22e

750 — 432e 17e 483e 19e 559e 22e 610e 24e

800 — 457 18 508 20 559 22 610 24

900 — 483 19 559 22 610 24 610 24

1000 — 508 20 — — — —

1250 — 559 22 — — — —

1500 — 610 24 — — — —

1750 — 610 24 — — — —

2000 — 610 24 — — — —

Notes:

1. Bending space at terminals shall be measured in a straight line from the end of the lug or wire connector in a direction perpendicular to the enclosure wall.

2. For removable and lay-in wire terminals intended for only one wire, bending space shall be permitted to be reduced by the following number of millimeters (inches):

a12.7 mm (1/2 in.)

b25.4 mm (1 in.)

c38.1 mm (11/2 in.)

d50.8 mm (2 in.)

e76.2 mm (3 in.)

3. This column shall be permitted to determine the required wire-bending space for compact stranded aluminum conductors in sizes up to 1000 kcmil and manufactured using AA-8000 series electrical grade aluminum alloy conductor material in accordance with 310.3(B).

(1) Conductors Not Entering or Leaving Opposite Wall

Table 312.6(A) shall apply where the conductor does not enter or leave the enclosure through the wall opposite its terminal.

(2) Conductors Entering or Leaving Opposite Wall

Table 312.6(B) shall apply where the conductor does enter or leave the enclosure through the wall opposite its terminal.

Exception No. 1: Where the distance between the wall and its terminal is in accordance with Table 312.6(A), a conductor shall be permitted to enter or leave an enclosure through the wall opposite its terminal, provided the conductor enters or leaves the enclosure where the gutter joins an adjacent gutter that has a width that conforms to Table 312.6(B) for the conductor.

Exception No. 2: A conductor not larger than 350 kcmil shall be permitted to enter or leave an enclosure containing only a meter socket(s) through the wall opposite its terminal, provided the distance between the terminal and the opposite wall is not less than that specified in Table 312.6(A) and the terminal is a lay-in type or removable lug with integral mounting tang, where the terminal is either of the following:

Directed toward the opening in the enclosure and within a 45-degree angle of directly facing the enclosure wall

Directly facing the enclosure wall and offset not greater than 50 percent of the bending space specified in Table 312.6(A)

Informational Note: Offset is the distance measured along the enclosure wall from the axis of the centerline of the terminal to a line passing through the center of the opening in the enclosure.

(C) Conductors 4 AWG or Larger

Installation shall comply with 300.4(G).

312.7 Space in Enclosures

Cabinets and cutout boxes shall have approved space to accommodate all conductors installed in them without crowding.

312.8 Switch and Overcurrent Device Enclosures

The wiring space within enclosures for switches and overcurrent devices shall be permitted for other wiring and equipment subject to limitations for specific equipment as provided in 312.8(A) and (B).

(A) Splices, Taps, and Feed-Through Conductors

The wiring space of enclosures for switches or overcurrent devices shall be permitted for conductors feeding through, spliced, or tapping off to other enclosures, switches, or overcurrent devices where all of the following conditions are met:

The total of all conductors installed at any cross section of the wiring space does not exceed 40 percent of the cross-sectional area of that space.

The total area of all conductors, splices, and taps installed at any cross section of the wiring space does not exceed 75 percent of the cross-sectional area of that space.

A warning label complying with 110.21(B) is applied to the enclosure that identifies the closest disconnecting means for any feed-through conductors.

(B) Power Monitoring or Energy Management Equipment

The wiring space of enclosures for switches or overcurrent devices shall be permitted to contain power monitoring or energy management equipment in accordance with 312.8(B)(1) through (B)(3).

(1) Identification

The power monitoring or energy management equipment shall be identified as a field installable accessory as part of the listed equipment or is a listed kit evaluated for field installation in switch or overcurrent device enclosures.

(2) Area

The total area of all conductors, splices, taps, and equipment at any cross section of the wiring space shall not exceed 75 percent of the cross-sectional area of that space.

(3) Conductors

Conductors used exclusively for control or instrumentation circuits shall comply with either 312.8(B)(3)(a) or (B)(3)(b).

(a) Conductors shall comply with 725.49.

(b) Conductors smaller than 18 AWG, but not smaller than 22 AWG for a single conductor and 26 AWG for a multiconductor cable, shall be permitted to be used where the conductors and cable assemblies meet all of the following conditions:

Are enclosed within raceways or routed along one or more walls of the enclosure and secured at intervals that do not exceed 250 mm (10 in.)

Are secured within 250 mm (10 in.) of terminations

Are secured to prevent contact with current carrying components within the enclosure

Are rated for the system voltage and not less than 600 volts

Have a minimum insulation temperature rating of 90°C

312.9 Side or Back Wiring Spaces or Gutters

Cabinets and cutout boxes shall be provided with back-wiring spaces, gutters, or wiring compartments as required by 312.11(C) and (D).

Part II Construction Specifications

312.10 Material

Cabinets, cutout boxes, and meter socket enclosures shall comply with 312.10(A) through (C).

(A) Metal Cabinets and Cutout Boxes

Metal enclosures within the scope of this article shall be protected both inside and outside against corrosion.

(B) Strength

The design and construction of enclosures within the scope of this article shall be such as to secure ample strength and rigidity. If constructed of sheet steel, the metal thickness shall not be less than 1.35 mm (0.053 in.) uncoated.

(C) Nonmetallic Cabinets

Nonmetallic cabinets shall be listed, or they shall be submitted for approval prior to installation.

312.11 Spacing

The spacing within cabinets and cutout boxes shall comply with 312.11(A) through (D).

(A) General

Spacing within cabinets and cutout boxes shall provide approved spacing for the distribution of wires and cables placed in them and for a separation between metal parts of devices and apparatus mounted within them in accordance with 312.11(A)(1), (A)(2), and (A)(3).

(1) Base

Other than at points of support, there shall be an airspace of at least 1.59 mm (0.0625 in.) between the base of the device and the wall of any metal cabinet or cutout box in which the device is mounted.

(2) Doors

There shall be an airspace of at least 25.4 mm (1.00 in.) between any live metal part, including live metal parts of enclosed fuses, and the door.

Exception: Where the door is lined with an approved insulating material or is of a thickness of metal not less than 2.36 mm (0.093 in.) uncoated, the airspace shall not be less than 12.7 mm (0.500 in.).

(3) Live Parts

There shall be an airspace of at least 12.7 mm (0.500 in.) between the walls, back, gutter partition, if of metal, or door of any cabinet or cutout box and the nearest exposed current-carrying part of devices mounted within the cabinet where the voltage does not exceed 250. This spacing shall be increased to at least 25.4 mm (1.00 in.) for voltages of 251 to 1000, nominal.

Exception: Where the conditions in 312.11(A)(2), Exception, are met, the airspace for nominal voltages from 251 to 600 shall be permitted to be not less than 12.7 mm (0.500 in.).

(B) Switch Clearance

Cabinets and cutout boxes shall be deep enough to allow the closing of the doors when 30-ampere branch-circuit panelboard switches are in any position, when combination cutout switches are in any position, or when other single-throw switches are opened as far as their construction permits.

(C) Wiring Space

Cabinets and cutout boxes that contain devices or apparatus connected within the cabinet or box to more than eight conductors, including those of branch circuits, meter loops, feeder circuits, power circuits, and similar circuits, but not including the supply circuit or a continuation thereof, shall have back-wiring spaces or one or more side-wiring spaces, side gutters, or wiring compartments.

(D) Wiring Space — Enclosure

Side-wiring spaces, side gutters, or side-wiring compartments of cabinets and cutout boxes shall be made tight enclosures by means of covers, barriers, or partitions extending from the bases of the devices contained in the cabinet, to the door, frame, or sides of the cabinet.

Exception: Side-wiring spaces, side gutters, and side-wiring compartments of cabinets shall not be required to be made tight enclosures where those side spaces contain only conductors that enter the cabinet directly opposite to the devices where they terminate.

Partially enclosed back-wiring spaces shall be provided with covers to complete the enclosure. Wiring spaces that are required by 312.11(C) and are exposed when doors are open shall be provided with covers to complete the enclosure. Where space is provided for feed-through conductors and for splices as required in 312.8, additional barriers shall not be required.

Article 314 Outlet, Device, Pull, and Junction Boxes; Conduit Bodies; Fittings; And Handhole Enclosures

Part I Scope and General

314.1 Scope

This article covers the installation and use of all boxes and conduit bodies used as outlet, device, junction, or pull boxes, depending on their use, and handhole enclosures. Cast metal, sheet metal, nonmetallic, and other boxes such as FS, FD, and larger boxes are not classified as conduit bodies. This article also includes installation requirements for fittings used to join raceways and to connect raceways and cables to boxes and conduit bodies.

314.2 Round Boxes

Round boxes shall not be used where conduits or connectors requiring the use of locknuts or bushings are to be connected to the side of the box.

314.3 Nonmetallic Boxes

Nonmetallic boxes shall be permitted only with open wiring on insulators, concealed knob-and-tube wiring, cabled wiring methods with entirely nonmetallic sheaths, flexible cords, and nonmetallic raceways.

Exception No. 1: Where internal bonding means are provided between all entries, nonmetallic boxes shall be permitted to be used with metal raceways or metal-armored cables.

Exception No. 2: Where integral bonding means with a provision for attaching an equipment bonding jumper inside the box are provided between all threaded entries in nonmetallic boxes listed for the purpose, nonmetallic boxes shall be permitted to be used with metal raceways or metal-armored cables.

314.4 Metal Boxes

Metal boxes shall be grounded and bonded in accordance with Parts I, IV, V, VI, VII, and X of Article 250 as applicable, except as permitted in 250.112(I).

Part II Installation

314.15 Damp or Wet Locations

In damp or wet locations, boxes, conduit bodies, outlet box hoods, and fittings shall be placed or equipped so as to prevent moisture from entering or accumulating within the box, conduit body, or fitting. Boxes, conduit bodies, outlet box hoods, and fittings installed in wet locations shall be listed for use in wet locations. Approved drainage openings not smaller than 3 mm (1/8 in.) and not larger than 6 mm (1/4 in.) in diameter shall be permitted to be installed in the field in boxes or conduit bodies listed for use in damp or wet locations. For installation of listed drain fittings, larger openings are permitted to be installed in the field in accordance with manufacturer's instructions.

Informational Note No. 1: For boxes in floors, see 314.27(B).

Informational Note No. 2: For protection against corrosion, see 300.6.

314.16 Number of Conductors in Outlet, Device, and Junction Boxes, and Conduit Bodies

Boxes and conduit bodies shall be of an approved size to provide free space for all enclosed conductors. In no case shall the volume of the box, as calculated in 314.16(A), be less than the fill calculation as calculated in 314.16(B). The minimum volume for conduit bodies shall be as calculated in 314.16(C).

The provisions of this section shall not apply to terminal housings supplied with motors or generators.

Informational Note: For volume requirements of motor or generator terminal housings, see 430.12.

Boxes and conduit bodies enclosing conductors 4 AWG or larger shall also comply with the provisions of 314.28. Outlet and device boxes shall also comply with 314.24.

(A) Box Volume Calculations

The volume of a wiring enclosure (box) shall be the total volume of the assembled sections and, where used, the space provided by plaster rings, domed covers, extension rings, and so forth, that are marked with their volume or are made from boxes the dimensions of which are listed in Table 314.16(A). Where a box is provided with one or more securely installed barriers, the volume shall be apportioned to each of the resulting spaces. Each barrier, if not marked with its volume, shall be considered to take up 8.2 cm3 (1/2 in.3) if metal, and 16.4 cm3 (1.0 in.3) if nonmetallic.

Table 314.16(A) Metal Boxes

Box Trade Size Minimum Volume Maximum Number of Conductors\*

(arranged by AWG size)

mm in. cm3 in.3 18 16 14 12 10 8 6

100 × 32 (4 × 11/4) round/octagonal 205 12.5

8

7 6 5 5 5 2

100 × 38 (4 × 11/2) round/octagonal 254 15.5 10 8 7 6 6 5 3

100 × 54 (4 × 21/8) round/octagonal 353 21.5 14 12 10 9 8 7 4

100 × 32 (4 × 11/4) square 295 18.0 12 10 9 8 7 6 3

100 × 38 (4 × 11/2) square 344 21.0 14 12 10 9 8 7 4

100 × 54 (4 × 21/8) square 497 30.3 20 17 15 13 12 10 6

120 × 32 (411/16 × 11/4) square 418 25.5 17 14 12 11 10 8 5

120 × 38 (411/16 × 11/2) square 484 29.5 19 16 14 13 11 9 5

120 × 54 (411/16 × 21/8) square 689 42.0 28 24 21 18 16 14 8

75 × 50 × 38 (3 × 2 × 11/2) device 123 7.5 5 4 3 3 3 2 1

75 × 50 × 50 (3 × 2 × 2) device 164 10.0 6 5 5 4 4 3 2

75 × 50 × 57 (3 × 2 × 21/4) device 172 10.5 7 6 5 4 4 3 2

75 × 50 × 65 (3 × 2 × 21/2) device 205 12.5 8 7 6 5 5 4 2

75 × 50 × 70 (3 × 2 × 23/4) device 230 14.0 9 8 7 6 5 4 2

75 × 50 × 90 (3 × 2 × 31/2) device 295 18.0 12 10 9 8 7 6 3

100 × 54 × 38 (4 × 21/8 × 11/2) device 169 10.3 6 5 5 4 4 3 2

100 × 54 × 48 (4 × 21/8 × 17/8) device 213 13.0 8 7 6 5 5 4 2

100 × 54 × 54 (4 × 21/8 × 21/8) device 238 14.5 9 8 7 6 5 4 2

95 × 50 × 65 (33/4 × 2 × 21/2) masonry box/gang 230 14.0 9 8 7 6 5 4 2

95 × 50 × 90 (33/4 × 2 × 31/2) masonry box/gang 344 21.0 14 12 10 9 8 7 4

min. 44.5 depth FS — single cover/gang (13/4) 221 13.5 9 7 6 6 5 4 2

min. 60.3 depth FD — single cover/gang (23/8) 295 18.0 12 10 9 8 7 6 3

min. 44.5 depth FS — multiple cover/gang (13/4) 295 18.0 12 10 9 8 7 6 3

min. 60.3 depth FD — multiple cover/gang (23/8) 395 24.0 16 13 12 10 9 8 4

\*Where no volume allowances are required by 314.16(B)(2) through (B)(5).

(1) Standard Boxes

The volumes of standard boxes that are not marked with their volume shall be as given in Table 314.16(A).

(2) Other Boxes

Boxes 1650 cm3 (100 in.3) or less, other than those described in Table 314.16(A), and nonmetallic boxes shall be durably and legibly marked by the manufacturer with their volume(s). Boxes described in Table 314.16(A) that have a volume larger than is designated in the table shall be permitted to have their volume marked as required by this section.

(B) Box Fill Calculations

The volumes in paragraphs 314.16(B)(1) through (B)(5), as applicable, shall be added together. No allowance shall be required for small fittings such as locknuts and bushings. Each space within a box installed with a barrier shall be calculated separately.

Table 314.16(B) Volume Allowance Required per Conductor

Size of Conductor (AWG) Free Space Within Box for Each Conductor

cm3 in.3

18 24.6 1.50

16 28.7 1.75

14 32.8 2.00

12 36.9 2.25

10 41.0 2.50

8 49.2 3.00

6 81.9 5.00

(1) Conductor Fill

Each conductor that originates outside the box and terminates or is spliced within the box shall be counted once, and each conductor that passes through the box without splice or termination shall be counted once. Each loop or coil of unbroken conductor not less than twice the minimum length required for free conductors in 300.14 shall be counted twice. The conductor fill shall be calculated using Table 314.16(B). A conductor, no part of which leaves the box, shall not be counted.

Exception: An equipment grounding conductor or conductors or not over four fixture wires smaller than 14 AWG, or both, shall be permitted to be omitted from the calculations where they enter a box from a domed luminaire or similar canopy and terminate within that box.

(2) Clamp Fill

Where one or more internal cable clamps, whether factory or field supplied, are present in the box, a single volume allowance in accordance with Table 314.16(B) shall be made based on the largest conductor present in the box. No allowance shall be required for a cable connector with its clamping mechanism outside the box.

A clamp assembly that incorporates a cable termination for the cable conductors shall be listed and marked for use with specific nonmetallic boxes. Conductors that originate within the clamp assembly shall be included in conductor fill calculations covered in 314.16(B)(1) as though they entered from outside the box. The clamp assembly shall not require a fill allowance, but the volume of the portion of the assembly that remains within the box after installation shall be excluded from the box volume as marked in 314.16(A)(2).

(3) Support Fittings Fill

Where one or more luminaire studs or hickeys are present in the box, a single volume allowance in accordance with Table 314.16(B) shall be made for each type of fitting based on the largest conductor present in the box.

(4) Device or Equipment Fill

For each yoke or strap containing one or more devices or equipment, a double volume allowance in accordance with Table 314.16(B) shall be made for each yoke or strap based on the largest conductor connected to a device(s) or equipment supported by that yoke or strap. A device or utilization equipment wider than a single 50 mm (2 in.) device box as described in Table 314.16(A) shall have double volume allowances provided for each gang required for mounting.

(5) Equipment Grounding Conductor Fill

Where up to four equipment grounding conductors or equipment bonding jumpers enter a box, a single volume allowance in accordance with Table 314.16(B) shall be made based on the largest equipment grounding conductor or equipment bonding jumper entering the box. A 1/4 volume allowance shall be made for each additional equipment grounding conductor or equipment bonding jumper that enters the box, based on the largest equipment grounding conductor or equipment bonding conductor.

(C) Conduit Bodies

(1) General

Conduit bodies enclosing 6 AWG conductors or smaller, other than short-radius conduit bodies as described in 314.16(C)(3), shall have a cross-sectional area not less than twice the cross-sectional area of the largest conduit or tubing to which they can be attached. The maximum number of conductors permitted shall be the maximum number permitted by Table 1 of Chapter 9 for the conduit or tubing to which it is attached.

(2) With Splices, Taps, or Devices

Only those conduit bodies that are durably and legibly marked by the manufacturer with their volume shall be permitted to contain splices, taps, or devices. The maximum number of conductors shall be calculated in accordance with 314.16(B). Conduit bodies shall be supported in a rigid and secure manner.

(3) Short Radius Conduit Bodies

Conduit bodies such as capped elbows and service-entrance elbows that enclose conductors 6 AWG or smaller, and are only intended to enable the installation of the raceway and the contained conductors, shall not contain splices, taps, or devices and shall be of an approved size to provide free space for all conductors enclosed in the conduit body.

314.17 Conductors Entering Boxes, Conduit Bodies, or Fittings

Conductors entering boxes, conduit bodies, or fittings shall be protected from abrasion and shall comply with 314.17(A) through (C).

(A) Openings to Be Closed

Openings through which conductors enter shall be closed in a manner identified for the application.

(B) Boxes and Conduit Bodies

The installation of the conductors in boxes and conduit bodies shall comply with 314.17(B)(1) through (B)(4).

(1) Conductors Entering Through Individual Holes or Through Flexible Tubing

For messenger-supported wiring, open wiring on insulators, or concealed knob-and-tube wiring, the conductors shall enter the box through individual holes. In installations where metal boxes or conduit bodies are used with conductors unprotected by flexible tubing, the individual openings shall be provided with insulating bushings. Where flexible tubing is used to enclose the conductors, the tubing shall extend from the last insulating support to not less than 6 mm (1/4 in.) inside the box or conduit body and beyond any cable clamp. The wiring method shall be secured to the box or conduit body.

(2) Conductors Entering Through Cable Clamps

Where cable assemblies with nonmetallic sheathes are used, the sheath shall extend not less than 6 mm (1/4 in.) inside the box and beyond any cable clamp. Except as provided in 300.15(C), the wiring method shall be secured to the box or conduit body.

Exception: Where nonmetallic-sheathed cable is used with single gang nonmetallic boxes not larger than a nominal size 57 mm × 100 mm (21/4 in. × 4 in.) mounted in walls or ceilings, and where the cable is fastened within 200 mm (8 in.) of the box measured along the sheath and where the sheath extends through a cable knockout not less than 6 mm (1/4 in.), securing the cable to the box shall not be required. Multiple cable entries shall be permitted in a single cable knockout opening.

(3) Conductors Entering Through Raceways

Where the raceway is complete between boxes, conduit bodies, or both and encloses individual conductors or nonmetallic cable assemblies or both, the conductors or cable assemblies shall not be required to be additionally secured. Where raceways enclose cable assemblies as provided in 300.15(C), the cable assembly shall not be required to be additionally secured within the box or conduit body.

(4) Temperature Limitation

Nonmetallic boxes and conduit bodies shall be suitable for the lowest temperature-rated conductor entering the box or conduit body.

(C) Conductors 4 AWG or Larger

Installation shall comply with 300.4(G).

Informational Note: See 110.12(A) for requirements on closing unused cable and raceway knockout openings.

314.19 Boxes Enclosing Flush Devices or Flush Equipment

Boxes used to enclose flush devices or flush equipment shall be of such design that the devices or equipment will be completely enclosed on the back and sides, and substantial support for the devices or equipment will be provided. Screws for supporting the box shall not also be used to attach a device or equipment.

314.20 Flush-Mounted Installations

Installations within or behind a surface of concrete, tile, gypsum, plaster, or other noncombustible material, including boxes employing a flushtype cover or faceplate, shall be made so that the front edge of the box, plaster ring, extension ring, or listed extender will not be set back of the finished surface more than 6 mm (1/4 in.).

Installations within a surface of wood or other combustible surface material, boxes, plaster rings, extension rings, or listed extenders shall extend to the finished surface or project therefrom.

314.21 Repairing Noncombustible Surfaces

Noncombustible surfaces that are broken or incomplete around boxes employing a flush-type cover or faceplate shall be repaired so there will be no gaps or open spaces greater than 3 mm (1/8 in.) at the edge of the box.

314.22 Surface Extensions

Surface extensions shall be made by mounting and mechanically securing an extension ring over the box. Equipment grounding shall be in accordance with Part VI of Article 250.

Exception: A surface extension shall be permitted to be made from the cover of a box where the cover is designed so it is unlikely to fall off or be removed if its securing means becomes loose. The wiring method shall be flexible for an approved length that permits removal of the cover and provides access to the box interior and shall be arranged so that any grounding continuity is independent of the connection between the box and cover.

314.23 Supports

Enclosures within the scope of this article shall be supported in accordance with one or more of the provisions in 314.23(A) through (H).

(A) Surface Mounting

An enclosure mounted on a building or other surface shall be rigidly and securely fastened in place. If the surface does not provide rigid and secure support, additional support in accordance with other provisions of this section shall be provided.

(B) Structural Mounting

An enclosure supported from a structural member or from grade shall be rigidly supported either directly or by using a metal, polymeric, or wood brace.

(1) Nails and Screws

Nails and screws, where used as a fastening means, shall secure boxes by using brackets on the outside of the enclosure, or by using mounting holes in the back or in one or more sides of the enclosure, or they shall pass through the interior within 6 mm (1/4 in.) of the back or ends of the enclosure. Screws shall not be permitted to pass through the box unless exposed threads in the box are protected using approved means to avoid abrasion of conductor insulation. Mounting holes made in the field shall be approved.

(2) Braces

Metal braces shall be protected against corrosion and formed from metal that is not less than 0.51 mm (0.020 in.) thick uncoated. Wood braces shall have a cross section not less than nominal 25 mm × 50 mm (1 in. × 2 in.). Wood braces in wet locations shall be treated for the conditions. Polymeric braces shall be identified as being suitable for the use.

(C) Mounting in Finished Surfaces

An enclosure mounted in a finished surface shall be rigidly secured thereto by clamps, anchors, or fittings identified for the application.

(D) Suspended Ceilings

An enclosure mounted to structural or supporting elements of a suspended ceiling shall be not more than 1650 cm3 (100 in.3) in size and shall be securely fastened in place in accordance with either 314.23(D)(1) or (D)(2).

(1) Framing Members

An enclosure shall be fastened to the framing members by mechanical means such as bolts, screws, or rivets, or by the use of clips or other securing means identified for use with the type of ceiling framing member(s) and enclosure(s) employed. The framing members shall be supported in an approved manner and securely fastened to each other and to the building structure.

(2) Support Wires

The installation shall comply with 300.11(A). The enclosure shall be secured, using identified methods, to ceiling support wire(s), including any additional support wire(s) installed for ceiling support. Support wire(s) used for enclosure support shall be fastened at each end so as to be taut within the ceiling cavity.

(E) Raceway-Supported Enclosure, Without Devices, Luminaires, or Lampholders

An enclosure that does not contain a device(s), other than splicing devices, or supports a luminaire(s), a lampholder, or other equipment and is supported by entering raceways shall not exceed 1650 cm3 (100 in.3) in size. It shall have threaded entries or identified hubs. It shall be supported by two or more conduits threaded wrenchtight into the enclosure or hubs. Each conduit shall be secured within 900 mm (3 ft) of the enclosure, or within 450 mm (18 in.) of the enclosure if all conduit entries are on the same side.

Exception: The following wiring methods shall be permitted to support a conduit body of any size, including a conduit body constructed with only one conduit entry, provided that the trade size of the conduit body is not larger than the largest trade size of the conduit or tubing:

Intermediate metal conduit, Type IMC

Rigid metal conduit, Type RMC

Rigid polyvinyl chloride conduit, Type PVC

Reinforced thermosetting resin conduit, Type RTRC

Electrical metallic tubing, Type EMT

(F) Raceway-Supported Enclosures, With Devices, Luminaires, or Lampholders

An enclosure that contains a device(s), other than splicing devices, or supports a luminaire(s), a lampholder, or other equipment and is supported by entering raceways shall not exceed 1650 cm3 (100 in.3) in size. It shall have threaded entries or identified hubs. It shall be supported by two or more conduits threaded wrenchtight into the enclosure or hubs. Each conduit shall be secured within 450 mm (18 in.) of the enclosure.

Exception No. 1: Rigid metal or intermediate metal conduit shall be permitted to support a conduit body of any size, including a conduit body constructed with only one conduit entry, provided the trade size of the conduit body is not larger than the largest trade size of the conduit.

Exception No. 2: An unbroken length(s) of rigid or intermediate metal conduit shall be permitted to support a box used for luminaire or lampholder support, or to support a wiring enclosure that is an integral part of a luminaire and used in lieu of a box in accordance with 300.15(B), where all of the following conditions are met:

The conduit is securely fastened at a point so that the length of conduit beyond the last point of conduit support does not exceed 900 mm (3 ft).

The unbroken conduit length before the last point of conduit support is 300 mm (12 in.) or greater, and that portion of the conduit is securely fastened at some point not less than 300 mm (12 in.) from its last point of support.

Where accessible to unqualified persons, the luminaire or lampholder, measured to its lowest point, is at least 2.5 m (8 ft) above grade or standing area and at least 900 mm (3 ft) measured horizontally to the 2.5 m (8 ft) elevation from windows, doors, porches, fire escapes, or similar locations.

A luminaire supported by a single conduit does not exceed 300 mm (12 in.) in any direction from the point of conduit entry.

The weight supported by any single conduit does not exceed 9 kg (20 lb).

At the luminaire or lampholder end, the conduit(s) is threaded wrenchtight into the box, conduit body, integral wiring enclosure, or identified hubs. Where a box or conduit body is used for support, the luminaire shall be secured directly to the box or conduit body, or through a threaded conduit nipple not over 75 mm (3 in.) long.

(G) Enclosures in Concrete or Masonry

An enclosure supported by embedment shall be identified as suitably protected from corrosion and securely embedded in concrete or masonry.

(H) Pendant Boxes

An enclosure supported by a pendant shall comply with 314.23(H)(1) or (H)(2).

(1) Flexible Cord

A box shall be supported from a multiconductor cord or cable in an approved manner that protects the conductors against strain, such as a strain-relief connector threaded into a box with a hub.

(2) Conduit

A box supporting lampholders or luminaires, or wiring enclosures within luminaires used in lieu of boxes in accordance with 300.15(B), shall be supported by rigid or intermediate metal conduit stems. For stems longer than 450 mm (18 in.), the stems shall be connected to the wiring system with listed swivel hangers suitable for the location. At the luminaire end, the conduit(s) shall be threaded wrenchtight into the box, wiring enclosure, or identified hubs.

Where supported by only a single conduit, the threaded joints shall be prevented from loosening by the use of set-screws or other effective means, or the luminaire, at any point, shall be at least 2.5 m (8 ft) above grade or standing area and at least 900 mm (3 ft) measured horizontally to the 2.5 m (8 ft) elevation from windows, doors, porches, fire escapes, or similar locations. A luminaire supported by a single conduit shall not exceed 300 mm (12 in.) in any horizontal direction from the point of conduit entry.

314.24 Depth of Boxes

Outlet and device boxes shall have an approved depth to allow equipment installed within them to be mounted properly and without likelihood of damage to conductors within the box.

(A) Outlet Boxes Without Enclosed Devices or Utilization Equipment

Outlet boxes that do not enclose devices or utilization equipment shall have a minimum internal depth of 12.7 mm (1/2 in.).

(B) Outlet and Device Boxes With Enclosed Devices or Utilization Equipment

Outlet and device boxes that enclose devices or utilization equipment shall have a minimum internal depth that accommodates the rearward projection of the equipment and the size of the conductors that supply the equipment. The internal depth shall include, where used, that of any extension boxes, plaster rings, or raised covers. The internal depth shall comply with all applicable provisions of 314.24(B)(1) through (B)(5).

(1) Large Equipment

Boxes that enclose devices or utilization equipment that projects more than 48 mm (17/8 in.) rearward from the mounting plane of the box shall have a depth that is not less than the depth of the equipment plus 6 mm (1/4 in.).

(2) Conductors Larger Than 4 AWG

Boxes that enclose devices or utilization equipment supplied by conductors larger than 4 AWG shall be identified for their specific function.

Exception to (2): Devices or utilization equipment supplied by conductors larger than 4 AWG shall be permitted to be mounted on or in junction and pull boxes larger than 1650 cm3 (100 in.3) if the spacing at the terminals meets the requirements of 312.6.

(3) Conductors 8, 6, or 4 AWG

Boxes that enclose devices or utilization equipment supplied by 8, 6, or 4 AWG conductors shall have an internal depth that is not less than 52.4 mm (21/16 in.).

(4) Conductors 12 or 10 AWG

Boxes that enclose devices or utilization equipment supplied by 12 or 10 AWG conductors shall have an internal depth that is not less than 30.2 mm (13/16 in.). Where the equipment projects rearward from the mounting plane of the box by more than 25 mm (1 in.), the box shall have a depth not less than that of the equipment plus 6 mm (1/4 in.).

(5) Conductors 14 AWG and Smaller

Boxes that enclose devices or utilization equipment supplied by 14 AWG or smaller conductors shall have a depth that is not less than 23.8 mm (15/16 in.).

Exception to (1) through (5): Devices or utilization equipment that is listed to be installed with specified boxes shall be permitted.

314.25 Covers and Canopies

In completed installations, each box shall have a cover, faceplate, lampholder, or luminaire canopy, except where the installation complies with 410.24(B). Screws used for the purpose of attaching covers, or other equipment, to the box shall be either machine screws matching the thread gauge and size that is integral to the box or shall be in accordance with the manufacturer's instructions.

(A) Nonmetallic or Metal Covers and Plates

Nonmetallic or metal covers and plates shall be permitted. Where metal covers or plates are used, they shall comply with the grounding requirements of 250.110.

Informational Note: For additional grounding requirements, see 410.42 for metal luminaire canopies, and 404.12 and 406.6(B) for metal faceplates.

(B) Exposed Combustible Wall or Ceiling Finish

Where a luminaire canopy or pan is used, any combustible wall or ceiling finish exposed between the edge of the canopy or pan and the outlet box shall be covered with noncombustible material if required by 410.23.

(C) Flexible Cord Pendants

Covers of outlet boxes and conduit bodies having holes through which flexible cord pendants pass shall be provided with identified bushings or shall have smooth, well-rounded surfaces on which the cords may bear. So-called hard rubber or composition bushings shall not be used.

314.27 Outlet Boxes

(A) Boxes at Luminaire or Lampholder Outlets

Outlet boxes or fittings designed for the support of luminaires and lampholders, and installed as required by 314.23, shall be permitted to support a luminaire or lampholder.

(1) Vertical Surface Outlets

Boxes used at luminaire or lampholder outlets in or on a vertical surface shall be identified and marked on the interior of the box to indicate the maximum weight of the luminaire that is permitted to be supported by the box if other than 23 kg (50 lb).

Exception: A vertically mounted luminaire or lampholder weighing not more than 3 kg (6 lb) shall be permitted to be supported on other boxes or plaster rings that are secured to other boxes, provided that the luminaire or its supporting yoke, or the lampholder, is secured to the box with no fewer than two No. 6 or larger screws.

(2) Ceiling Outlets

At every outlet used exclusively for lighting, the box shall be designed or installed so that a luminaire or lampholder may be attached. Boxes shall be required to support a luminaire weighing a minimum of 23 kg (50 lb). A luminaire that weighs more than 23 kg (50 lb) shall be supported independently of the outlet box, unless the outlet box is listed for not less than the weight to be supported. The interior of the box shall be marked by the manufacturer to indicate the maximum weight the box shall be permitted to support.

(B) Floor Boxes

Boxes listed specifically for this application shall be used for receptacles located in the floor.

Exception: Where the authority having jurisdiction judges them free from likely exposure to physical damage, moisture, and dirt, boxes located in elevated floors of show windows and similar locations shall be permitted to be other than those listed for floor applications. Receptacles and covers shall be listed as an assembly for this type of location.

(C) Boxes at Ceiling-Suspended (Paddle) Fan Outlets

Outlet boxes or outlet box systems used as the sole support of a ceiling-suspended (paddle) fan shall be listed, shall be marked by their manufacturer as suitable for this purpose, and shall not support ceiling-suspended (paddle) fans that weigh more than 32 kg (70 lb). For outlet boxes or outlet box systems designed to support ceiling-suspended (paddle) fans that weigh more than 16 kg (35 lb), the required marking shall include the maximum weight to be supported.

Outlet boxes mounted in the ceilings of habitable rooms of dwelling occupancies in a location acceptable for the installation of a ceiling-suspended (paddle) fan shall comply with one of the following:

Listed for the sole support of ceiling-suspended (paddle) fans

An outlet box complying with the applicable requirements of 314.27 and providing access to structural framing capable of supporting of a ceiling-suspended (paddle) fan bracket or equivalent

(D) Utilization Equipment

Boxes used for the support of utilization equipment other than ceiling-suspended (paddle) fans shall meet the requirements of 314.27(A) for the support of a luminaire that is the same size and weight.

Exception: Utilization equipment weighing not more than 3 kg (6 lb) shall be permitted to be supported on other boxes or plaster rings that are secured to other boxes, provided the equipment or its supporting yoke is secured to the box with no fewer than two No. 6 or larger screws.

(E) Separable Attachment Fittings

Outlet boxes required in 314.27 shall be permitted to support listed locking support and mounting receptacles used in combination with compatible attachment fittings. The combination shall be identified for the support of equipment within the weight and mounting orientation limits of the listing. Where the supporting receptacle is installed within a box, it shall be included in the fill calculation covered in 314.16(B)(4).

314.28 Pull and Junction Boxes and Conduit Bodies

Boxes and conduit bodies used as pull or junction boxes shall comply with 314.28(A) through (E).

Exception: Terminal housings supplied with motors shall comply with the provisions of 430.12.

(A) Minimum Size

For raceways containing conductors of 4 AWG or larger that are required to be insulated, and for cables containing conductors of 4 AWG or larger, the minimum dimensions of pull or junction boxes installed in a raceway or cable run shall comply with 314.28(A)(1) through (A)(3). Where an enclosure dimension is to be calculated based on the diameter of entering raceways, the diameter shall be the metric designator (trade size) expressed in the units of measurement employed.

(1) Straight Pulls

In straight pulls, the length of the box or conduit body shall not be less than eight times the metric designator (trade size) of the largest raceway.

(2) Angle or U Pulls, or Splices

Where splices or where angle or U pulls are made, the distance between each raceway entry inside the box or conduit body and the opposite wall of the box or conduit body shall not be less than six times the metric designator (trade size) of the largest raceway in a row. This distance shall be increased for additional entries by the amount of the sum of the diameters of all other raceway entries in the same row on the same wall of the box. Each row shall be calculated individually, and the single row that provides the maximum distance shall be used.

Exception: Where a raceway or cable entry is in the wall of a box or conduit body opposite a removable cover, the distance from that wall to the cover shall be permitted to comply with the distance required for one wire per terminal in Table 312.6(A).

The distance between raceway entries enclosing the same conductor shall not be less than six times the metric designator (trade size) of the larger raceway.

When transposing cable size into raceway size in 314.28(A)(1) and (A)(2), the minimum metric designator (trade size) raceway required for the number and size of conductors in the cable shall be used.

(3) Smaller Dimensions

Listed boxes or listed conduit bodies of dimensions less than those required in 314.28(A)(1) and (A)(2) shall be permitted for installations of combinations of conductors that are less than the maximum conduit or tubing fill (of conduits or tubing being used) permitted by Table 1 of Chapter 9.

Listed conduit bodies of dimensions less than those required in 314.28(A)(2), and having a radius of the curve to the centerline not less than that indicated in Table 2 of Chapter 9 for one-shot and full-shoe benders, shall be permitted for installations of combinations of conductors permitted by Table 1 of Chapter 9. These conduit bodies shall be marked to show they have been specifically evaluated in accordance with this provision.

Where the permitted combinations of conductors for which the box or conduit body has been listed are less than the maximum conduit or tubing fill permitted by Table 1 of Chapter 9, the box or conduit body shall be permanently marked with the maximum number and maximum size of conductors permitted. For other conductor sizes and combinations, the total cross-sectional area of the fill shall not exceed the cross-sectional area of the conductors specified in the marking, based on the type of conductor identified as part of the product listing.

Informational Note: Unless otherwise specified, the applicable product standards evaluate the fill markings covered here based on conductors with Type XHHW insulation.

(B) Conductors in Pull or Junction Boxes

In pull boxes or junction boxes having any dimension over 1.8 m (6 ft), all conductors shall be cabled or racked up in an approved manner.

(C) Covers

All pull boxes, junction boxes, and conduit bodies shall be provided with covers compatible with the box or conduit body construction and suitable for the conditions of use. Where used, metal covers shall comply with the grounding requirements of 250.110.

(D) Permanent Barriers

Where permanent barriers are installed in a box, each section shall be considered as a separate box.

(E) Power Distribution Blocks

Power distribution blocks shall be permitted in pull and junction boxes over 1650 cm3 (100 in.3) for connections of conductors where installed in boxes and where the installation complies with 314.28(E)(1) through (E)(5).

Exception: Equipment grounding terminal bars shall be permitted in smaller enclosures.

(1) Installation

Power distribution blocks installed in boxes shall be listed.

(2) Size

In addition to the overall size requirement in the first sentence of 314.28(A)(2), the power distribution block shall be installed in a box with dimensions not smaller than specified in the installation instructions of the power distribution block.

(3) Wire Bending Space

Wire bending space at the terminals of power distribution blocks shall comply with 312.6.

(4) Live Parts

Power distribution blocks shall not have uninsulated live parts exposed within a box, whether or not the box cover is installed.

(5) Through Conductors

Where the pull or junction boxes are used for conductors that do not terminate on the power distribution block(s), the through conductors shall be arranged so the power distribution block terminals are unobstructed following installation.

314.29 Boxes, Conduit Bodies, and Handhole Enclosures to Be Accessible

Boxes, conduit bodies, and handhole enclosures shall be installed so that wiring contained in them can be rendered accessible in accordance with 314.29(A) and (B).

(A) In Buildings and Other Structures

Boxes and conduit bodies shall be installed so the contained wiring can be accessed without removing any part of the building or structure.

(B) Underground

Underground boxes and handhole enclosures shall be installed so they are accessible without excavating sidewalks, paving, earth, or other substance that is to be used to establish the finished grade.

Exception: Listed boxes and handhole enclosures shall be permitted where covered by gravel, light aggregate, or noncohesive granulated soil if their location is effectively identified and accessible for excavation.

314.30 Handhole Enclosures

Handhole enclosures shall be designed and installed to withstand all loads likely to be imposed on them. They shall be identified for use in underground systems.

Informational Note: See ANSI/SCTE 77-2013, Specification for Underground Enclosure Integrity, for additional information on deliberate and nondeliberate traffic loading that can be expected to bear on underground enclosures.

(A) Size

Handhole enclosures shall be sized in accordance with 314.28(A) for conductors operating at 1000 volts or below, and in accordance with 314.71 for conductors operating at over 1000 volts. For handhole enclosures without bottoms where the provisions of 314.28(A)(2), Exception, or 314.71(B)(1), Exception No. 1, apply, the measurement to the removable cover shall be taken from the end of the conduit or cable assembly.

(B) Wiring Entries

Underground raceways and cable assemblies entering a handhole enclosure shall extend into the enclosure, but they shall not be required to be mechanically connected to the enclosure.

(C) Enclosed Wiring

All enclosed conductors and any splices or terminations, if present, shall be listed as suitable for wet locations.

(D) Covers

Handhole enclosure covers shall have an identifying mark or logo that prominently identifies the function of the enclosure, such as "electric." Handhole enclosure covers shall require the use of tools to open, or they shall weigh over 45 kg (100 lb). Metal covers and other exposed conductive surfaces shall be bonded in accordance with 250.92 if the conductors in the handhole are service conductors, or in accordance with 250.96(A) if the conductors in the handhole are feeder or branch-circuit conductors.

Part III Construction Specifications

314.40 Metal Boxes, Conduit Bodies, and Fittings

(A) Corrosion Resistant

Metal boxes, conduit bodies, and fittings shall be corrosion resistant or shall be well-galvanized, enameled, or otherwise properly coated inside and out to prevent corrosion.

Informational Note: See 300.6 for limitation in the use of boxes and fittings protected from corrosion solely by enamel.

(B) Thickness of Metal

Sheet steel boxes not over 1650 cm3 (100 in.3) in size shall be made from steel not less than 1.59 mm (0.0625 in.) thick. The wall of a malleable iron box or conduit body and a die-cast or permanent-mold cast aluminum, brass, bronze, or zinc box or conduit body shall not be less than 2.38 mm (3/32 in.) thick. Other cast metal boxes or conduit bodies shall have a wall thickness not less than 3.17 mm (1/8 in.).

Exception No. 1: Listed boxes and conduit bodies shown to have equivalent strength and characteristics shall be permitted to be made of thinner or other metals.

Exception No. 2: The walls of listed short radius conduit bodies, as covered in 314.16(C)(2), shall be permitted to be made of thinner metal.

(C) Metal Boxes Over 1650 cm3 (100 in.3)

Metal boxes over 1650 cm3 (100 in.3) in size shall be constructed so as to be of ample strength and rigidity. If of sheet steel, the metal thickness shall not be less than 1.35 mm (0.053 in.) uncoated.

(D) Equipment Grounding Conductor Provisions

A means shall be provided in each metal box for the connection of an equipment grounding conductor. The means shall be permitted to be a tapped hole or equivalent.

314.41 Covers

Metal covers shall be of the same material as the box or conduit body with which they are used, or they shall be lined with firmly attached insulating material that is not less than 0.79 mm (1/32 in.) thick, or they shall be listed for the purpose. Metal covers shall be the same thickness as the boxes or conduit body for which they are used, or they shall be listed for the purpose. Covers of porcelain or other approved insulating materials shall be permitted if of such form and thickness as to afford the required protection and strength.

314.42 Bushings

Covers of outlet boxes and conduit bodies having holes through which flexible cord pendants may pass shall be provided with approved bushings or shall have smooth, well-rounded surfaces on which the cord may bear. Where individual conductors pass through a metal cover, a separate hole equipped with a bushing of suitable insulating material shall be provided for each conductor. Such separate holes shall be connected by a slot as required by 300.20.

314.43 Nonmetallic Boxes

Provisions for supports or other mounting means for nonmetallic boxes shall be outside of the box, or the box shall be constructed so as to prevent contact between the conductors in the box and the supporting screws.

314.44 Marking

All boxes and conduit bodies, covers, extension rings, plaster rings, and the like shall be durably and legibly marked with the manufacturer's name or trademark.

Part IV Pull and Junction Boxes, Conduit Bodies, and Handhole Enclosures for Use on Systems Over 1000 Volts, Nominal

314.70 General

(A) Pull and Junction Boxes

Where pull and junction boxes are used on systems over 1000 volts, the installation shall comply with the provisions of Part IV and with the following general provisions of this article:

Part I, 314.2; 314.3; and 314.4

Part II, 314.15; 314.17; 314.20; 314.23(A), (B), or (G); 314.28(B); and 314.29

Part III, 314.40(A) and (C); and 314.41

(B) Conduit Bodies

Where conduit bodies are used on systems over 1000 volts, the installation shall comply with the provisions of Part IV and with the following general provisions of this article:

Part I, 314.4

Part II, 314.15; 314.17; 314.23(A), (E), or (G); 314.28(A)(3); and 314.29

Part III, 314.40(A) and 314.41

(C) Handhole Enclosures

Where handhole enclosures are used on systems over 1000 volts, the installation shall comply with the provisions of Part IV and with the following general provisions of this article:

Part I, 314.3 and 314.4

Part II, 314.15; 314.17; 314.23(G); 314.28(B); 314.29; and 314.30

314.71 Size of Pull and Junction Boxes, Conduit Bodies, and Handhole Enclosures

Pull and junction boxes and handhole enclosures shall provide approved space and dimensions for the installation of conductors, and they shall comply with the specific requirements of this section. Conduit bodies shall be permitted if they meet the dimensional requirements for boxes.

(A) For Straight Pulls

The length of the box shall not be less than 48 times the outside diameter, over sheath, of the largest shielded or lead-covered conductor or cable entering the box. The length shall not be less than 32 times the outside diameter of the largest nonshielded conductor or cable.

(B) For Angle or U Pulls

(1) Distance to Opposite Wall

The distance between each cable or conductor entry inside the box and the opposite wall of the box shall not be less than 36 times the outside diameter, over sheath, of the largest cable or conductor. This distance shall be increased for additional entries by the amount of the sum of the outside diameters, over sheath, of all other cables or conductor entries through the same wall of the box.

Exception No. 1: Where a conductor or cable entry is in the wall of a box opposite a removable cover, the distance from that wall to the cover shall be permitted to be not less than the bending radius for the conductors as provided in 300.34.

Exception No. 2: Where cables are nonshielded and not lead covered, the distance of 36 times the outside diameter shall be permitted to be reduced to 24 times the outside diameter.

(2) Distance Between Entry and Exit

The distance between a cable or conductor entry and its exit from the box shall not be less than 36 times the outside diameter, over sheath, of that cable or conductor.

Exception: Where cables are nonshielded and not lead covered, the distance of 36 times the outside diameter shall be permitted to be reduced to 24 times the outside diameter.

(C) Removable Sides

One or more sides of any pull box shall be removable.

314.72 Construction and Installation Requirements

(A) Corrosion Protection

Boxes shall be made of material inherently resistant to corrosion or shall be suitably protected, both internally and externally, by enameling, galvanizing, plating, or other means.

(B) Passing Through Partitions

Suitable bushings, shields, or fittings having smooth, rounded edges shall be provided where conductors or cables pass through partitions and at other locations where necessary.

(C) Complete Enclosure

Boxes shall provide a complete enclosure for the contained conductors or cables.

(D) Wiring Is Accessible

Boxes and conduit bodies shall be installed so that the conductors are accessible without removing any fixed part of the building or structure. Working space shall be provided in accordance with 110.34.

(E) Suitable Covers

Boxes shall be closed by suitable covers securely fastened in place. Underground box covers that weigh over 45 kg (100 lb) shall be considered meeting this requirement. Covers for boxes shall be permanently marked "DANGER — HIGH VOLTAGE — KEEP OUT." The marking shall be on the outside of the box cover and shall be readily visible. Letters shall be block type and at least 13 mm (1/2 in.) in height.

(F) Suitable for Expected Handling

Boxes and their covers shall be capable of withstanding the handling to which they are likely to be subjected.

Article 320 Armored Cable: Type AC

Part I General

320.1 Scope

This article covers the use, installation, and construction specifications for armored cable, Type AC.

320.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Armored Cable, Type AC. A fabricated assembly of insulated conductors in a flexible interlocked metallic armor. See 320.100.

320.6 Listing Requirements

Type AC cable and associated fittings shall be listed.

Part II Installation

320.10 Uses Permitted

Type AC cable shall be permitted as follows:

For feeders and branch circuits in both exposed and concealed installations

In cable trays

In dry locations

Embedded in plaster finish on brick or other masonry, except in damp or wet locations

To be run or fished in the air voids of masonry block or tile walls where such walls are not exposed or subject to excessive moisture or dampness

Informational Note: The "Uses Permitted" is not an all-inclusive list.

320.12 Uses Not Permitted

Type AC cable shall not be used as follows:

Where subject to physical damage

In damp or wet locations

In air voids of masonry block or tile walls where such walls are exposed or subject to excessive moisture or dampness

Where exposed to corrosive conditions

Embedded in plaster finish on brick or other masonry in damp or wet locations

320.15 Exposed Work

Exposed runs of cable, except as provided in 300.11(B), shall closely follow the surface of the building finish or of running boards. Exposed runs shall also be permitted to be installed on the underside of joists where supported at each joist and located so as not to be subject to physical damage.

320.17 Through or Parallel to Framing Members

Type AC cable shall be protected in accordance with 300.4(A), (C), and (D) where installed through or parallel to framing members.

320.23 In Accessible Attics

Type AC cables in accessible attics or roof spaces shall be installed as specified in 320.23(A) and (B).

(A) Cables Run Across the Top of Floor Joists

Where run across the top of floor joists, or within 2.1 m (7 ft) of the floor or floor joists across the face of rafters or studding, the cable shall be protected by guard strips that are at least as high as the cable. Where this space is not accessible by permanently installed stairs or ladders, protection shall only be required within 1.8 m (6 ft) of the nearest edge of the scuttle hole or attic entrance.

(B) Cable Installed Parallel to Framing Members

Where the cable is installed parallel to the sides of rafters, studs, or ceiling or floor joists, neither guard strips nor running boards shall be required, and the installation shall also comply with 300.4(D).

320.24 Bending Radius

Bends in Type AC cable shall be made such that the cable is not damaged. The radius of the curve of the inner edge of any bend shall not be less than five times the diameter of the Type AC cable.

320.30 Securing and Supporting

(A) General

Type AC cable shall be supported and secured by staples; cable ties listed and identified for securement and support; straps, hangers, or similar fittings; or other approved means designed and installed so as not to damage the cable.

(B) Securing

Unless otherwise permitted, Type AC cable shall be secured within 300 mm (12 in.) of every outlet box, junction box, cabinet, or fitting and at intervals not exceeding 1.4 m (41/2 ft).

(C) Supporting

Unless otherwise permitted, Type AC cable shall be supported at intervals not exceeding 1.4 m (41/2 ft).

Horizontal runs of Type AC cable installed in wooden or metal framing members or similar supporting means shall be considered supported and secured where such support does not exceed 1.4 m (41/2 ft) intervals.

(D) Unsupported Cables

Type AC cable shall be permitted to be unsupported and unsecured where the cable complies with any of the following:

Is fished between access points through concealed spaces in finished buildings or structures and supporting is impracticable

Is not more than 600 mm (2 ft) in length at terminals where flexibility is necessary

Is not more than 1.8 m (6 ft) in length from the last point of cable support to the point of connection to a luminaire(s) or other electrical equipment and the cable and point of connection are within an accessible ceiling

For the purposes of this section, Type AC cable fittings shall be permitted as a means of cable support.

320.40 Boxes and Fittings

At all points where the armor of AC cable terminates, a fitting shall be provided to protect wires from abrasion, unless the design of the outlet boxes or fittings is such as to afford equivalent protection, and, in addition, an insulating bushing or its equivalent protection shall be provided between the conductors and the armor. The connector or clamp by which the Type AC cable is fastened to boxes or cabinets shall be of such design that the insulating bushing or its equivalent will be visible for inspection. Where change is made from Type AC cable to other cable or raceway wiring methods, a box, fitting, or conduit body shall be installed at junction points as required in 300.15.

320.80 Ampacity

The ampacity shall be determined in accordance with 310.14.

(A) Thermal Insulation

Armored cable installed in thermal insulation shall have conductors rated at 90°C (194°F). The ampacity of cable installed in these applications shall not exceed that of a 60°C (140°F) rated conductor. The 90°C (194°F) rating shall be permitted to be used for ampacity adjustment and correction calculations; however, the ampacity shall not exceed that of a 60°C (140°F) rated conductor.

Where more than two Type AC cables containing two or more current-carrying conductors in each cable are installed in contact with thermal insulation, caulk, or sealing foam without maintaining spacing between cables, the ampacity of each conductor shall be adjusted in accordance with Table 310.15(C)(1).

(B) Cable Tray

The ampacity of Type AC cable installed in cable tray shall be determined in accordance with 392.80(A).

Part III Construction Specifications

320.100 Construction

Type AC cable shall have an armor of flexible metal tape and shall have an internal bonding strip of copper or aluminum in intimate contact with the armor for its entire length.

320.104 Conductors

Insulated conductors shall be of a type listed in Table 310.4(A) or those identified for use in this cable. In addition, the conductors shall have an overall moisture-resistant and fire-retardant fibrous covering. For Type ACT, a moisture-resistant fibrous covering shall be required only on the individual conductors.

320.108 Equipment Grounding Conductor

Type AC cable shall provide an adequate path for fault current as required by 250.4(A)(5) or (B)(4) to act as an equipment grounding conductor.

320.120 Marking

The cable shall be marked in accordance with 310.8, except that Type AC shall have ready identification of the manufacturer by distinctive external markings on the cable armor throughout its entire length.

Article 322 Flat Cable Assemblies: Type FC

Part I General

322.1 Scope

This article covers the use, installation, and construction specifications for flat cable assemblies, Type FC.

322.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Flat Cable Assembly, Type FC. An assembly of parallel conductors formed integrally with an insulating material web specifically designed for field installation in surface metal raceway.

322.6 Listing Requirements

Type FC and associated fittings shall be listed.

Part II Installation

322.10 Uses Permitted

Flat cable assemblies shall be permitted only as follows:

As branch circuits to supply suitable tap devices for lighting, small appliances, or small power loads. The rating of the branch circuit shall not exceed 30 amperes.

Where installed for exposed work.

In locations where they will not be subjected to physical damage. Where a flat cable assembly is installed less than 2.5 m (8 ft) above the floor or fixed working platform, it shall be protected by a cover identified for the use.

In surface metal raceways identified for the use. The channel portion of the surface metal raceway systems shall be installed as complete systems before the flat cable assemblies are pulled into the raceways.

322.12 Uses Not Permitted

Flat cable assemblies shall not be used as follows:

Where exposed to corrosive conditions, unless suitable for the application

In hoistways or on elevators or escalators

In any hazardous (classified) location, except as specifically permitted by other articles in this Code

Outdoors or in wet or damp locations unless identified for the use

322.30 Securing and Supporting

The flat cable assemblies shall be supported by means of their special design features, within the surface metal raceways.

The surface metal raceways shall be supported as required for the specific raceway to be installed.

322.40 Boxes and Fittings

(A) Dead Ends

Each flat cable assembly dead end shall be terminated in an end-cap device identified for the use.

The dead-end fitting for the enclosing surface metal raceway shall be identified for the use.

(B) Luminaire Hangers

Luminaire hangers installed with the flat cable assemblies shall be identified for the use.

(C) Fittings

Fittings to be installed with flat cable assemblies shall be designed and installed to prevent physical damage to the cable assemblies.

(D) Extensions

All extensions from flat cable assemblies shall be made by approved wiring methods, within the junction boxes, installed at either end of the flat cable assembly runs.

322.56 Splices and Taps

(A) Splices

Splices shall be made in listed junction boxes.

(B) Taps

Taps shall be made between any phase conductor and the grounded conductor or any other phase conductor by means of devices and fittings identified for the use. Tap devices shall be rated at not less than 15 amperes, or more than 300 volts to ground, and shall be color-coded in accordance with the requirements of 322.120(C).

Part III Construction Specifications

322.100 Construction

Flat cable assemblies shall consist of two, three, four, or five conductors.

322.104 Conductors

Flat cable assemblies shall have conductors of 10 AWG special stranded copper wires.

322.112 Insulation

The entire flat cable assembly shall be formed to provide a suitable insulation covering all the conductors and using one of the materials recognized in Table 310.4(A) for general branch-circuit wiring.

322.120 Marking

(A) Temperature Rating

In addition to the provisions of 310.8, Type FC cable shall have the temperature rating durably marked on the surface at intervals not exceeding 600 mm (24 in.).

(B) Identification of Grounded Conductor

The grounded conductor shall be identified throughout its length by means of a distinctive and durable white or gray marking.

Informational Note: The color gray may have been used in the past as an ungrounded conductor. Care should be taken when working on existing systems.

(C) Terminal Block Identification

Terminal blocks identified for the use shall have distinctive and durable markings for color or word coding. The grounded conductor section shall have a white marking or other suitable designation. The next adjacent section of the terminal block shall have a black marking or other suitable designation. The next section shall have a red marking or other suitable designation. The final or outer section, opposite the grounded conductor section of the terminal block, shall have a blue marking or other suitable designation.

Article 324 Flat Conductor Cable: Type FCC

Part I General

324.1 Scope

This article covers a field-installed wiring system for branch circuits incorporating Type FCC cable and associated accessories as defined by the article. The wiring system is designed for installation under carpet squares.

324.2 Definitions

The definitions in this section shall apply only within this article.

Bottom Shield. A protective layer that is installed between the floor and Type FCC flat conductor cable to protect the cable from physical damage and may or may not be incorporated as an integral part of the cable.

Cable Connector. A connector designed to join Type FCC cables without using a junction box.

FCC System. A complete wiring system for branch circuits that is designed for installation under carpet squares.

Informational Note: The FCC system includes Type FCC cable and associated shielding, connectors, terminators, adapters, boxes, and receptacles.

Insulating End. An insulator designed to electrically insulate the end of a Type FCC cable.

Metal Shield Connections. Means of connection designed to electrically and mechanically connect a metal shield to another metal shield, to a receptacle housing or self-contained device, or to a transition assembly.

Top Shield. A grounded metal shield covering under-carpet components of the FCC system for the purposes of providing protection against physical damage.

Transition Assembly. An assembly to facilitate connection of the FCC system to other wiring systems, incorporating (1) a means of electrical interconnection and (2) a suitable box or covering for providing electrical safety and protection against physical damage.

Type FCC Cable. Three or more flat copper conductors placed edge-to-edge and separated and enclosed within an insulating assembly.

324.6 Listing Requirements

Type FCC cable and associated fittings shall be listed.

Part II Installation

324.10 Uses Permitted

(A) Branch Circuits

Use of FCC systems shall be permitted both for general-purpose and appliance branch circuits and for individual branch circuits.

(B) Branch-Circuit Ratings

(1) Voltage

Voltage between ungrounded conductors shall not exceed 300 volts. Voltage between ungrounded conductors and the grounded conductor shall not exceed 150 volts.

(2) Current

General-purpose and appliance branch circuits shall have ratings not exceeding 20 amperes. Individual branch circuits shall have ratings not exceeding 30 amperes.

(C) Floors

Use of FCC systems shall be permitted on hard, sound, smooth, continuous floor surfaces made of concrete, ceramic, or composition flooring, wood, and similar materials.

(D) Walls

Use of FCC systems shall be permitted on wall surfaces in surface metal raceways.

(E) Damp Locations

Use of FCC systems in damp locations shall be permitted.

(F) Heated Floors

Materials used for floors heated in excess of 30°C (86°F) shall be identified as suitable for use at these temperatures.

(G) System Height

Any portion of an FCC system with a height above floor level exceeding 2.3 mm (0.090 in.) shall be tapered or feathered at the edges to floor level.

324.12 Uses Not Permitted

FCC systems shall not be used in the following locations:

Outdoors or in wet locations

Where subject to corrosive vapors

In any hazardous (classified) location

In residential buildings

In school and hospital buildings, other than administrative office areas

324.18 Crossings

Crossings of more than two Type FCC cable runs shall not be permitted at any one point. Crossings of a Type FCC cable over or under a flat communications or signal cable shall be permitted. In each case, a grounded layer of metal shielding shall separate the two cables, and crossings of more than two flat cables shall not be permitted at any one point.

324.30 Securing and Supporting

All FCC system components shall be firmly anchored to the floor or wall using an adhesive or mechanical anchoring system identified for this use. Floors shall be prepared to ensure adherence of the FCC system to the floor until the carpet squares are placed.

324.40 Boxes and Fittings

(A) Cable Connections and Insulating Ends

All Type FCC cable connections shall use connectors identified for their use, installed such that electrical continuity, insulation, and sealing against dampness and liquid spillage are provided. All bare cable ends shall be insulated and sealed against dampness and liquid spillage using listed insulating ends.

(B) Polarization of Connections

All receptacles and connections shall be constructed and installed so as to maintain proper polarization of the system.

(C) Shields

(1) Top Shield

A metal top shield shall be installed over all floor-mounted Type FCC cable, connectors, and insulating ends. The top shield shall completely cover all cable runs, corners, connectors, and ends.

(2) Bottom Shield

A bottom shield shall be installed beneath all Type FCC cable, connectors, and insulating ends.

(D) Connection to Other Systems

Power feed, grounding connection, and shield system connection between the FCC system and other wiring systems shall be accomplished in a transition assembly identified for this use.

(E) Metal-Shield Connectors

Metal shields shall be connected to each other and to boxes, receptacle housings, self-contained devices, and transition assemblies using metal-shield connectors.

324.41 Floor Coverings

Floor-mounted Type FCC cable, cable connectors, and insulating ends shall be covered with carpet squares not larger than 1.0 m (39.37 in.) square. Carpet squares that are adhered to the floor shall be attached with release-type adhesives.

324.42 Devices

(A) Receptacles

All receptacles, receptacle housings, and self-contained devices used with the FCC system shall be identified for this use and shall be connected to the Type FCC cable and metal shields. Connection from any equipment grounding conductor of the Type FCC cable shall be made to the shield system at each receptacle.

(B) Receptacles and Housings

Receptacle housings and self-contained devices designed either for floor mounting or for in-wall or on-wall mounting shall be permitted for use with the FCC system. Receptacle housings and self-contained devices shall incorporate means for facilitating entry and termination of Type FCC cable and for electrically connecting the housing or device with the metal shield. Receptacles and self-contained devices shall comply with 406.4. Power and communications outlets installed together in common housing shall be permitted in accordance with 805.133(A)(1)(c), Exception No. 2.

324.56 Splices and Taps

(A) FCC Systems Alterations

Alterations to FCC systems shall be permitted. New cable connectors shall be used at new connection points to make alterations. It shall be permitted to leave unused cable runs and associated cable connectors in place and energized. All cable ends shall be covered with insulating ends.

(B) Transition Assemblies

All transition assemblies shall be identified for their use. Each assembly shall incorporate means for facilitating entry of the Type FCC cable into the assembly, for connecting the Type FCC cable to grounded conductors, and for electrically connecting the assembly to the metal cable shields and to equipment grounding conductors.

324.60 Grounding and Bonding

All metal shields, boxes, receptacle housings, and self-contained devices shall be electrically continuous to the equipment grounding conductor of the supplying branch circuit. All such electrical connections shall be made with connectors identified for this use. The electrical resistivity of such shield system shall not be more than that of one conductor of the Type FCC cable used in the installation.

Part III Construction Specifications

324.100 Construction

(A) Type FCC Cable

Type FCC cable shall be listed for use with the FCC system and shall consist of three, four, or five flat copper conductors, one of which shall be an equipment grounding conductor.

(B) Shields

(1) Materials and Dimensions

All top and bottom shields shall be of designs and materials identified for their use. Top shields shall be metal. Both metallic and nonmetallic materials shall be permitted for bottom shields.

(2) Resistivity

Metal shields shall have cross-sectional areas that provide for electrical resistivity of not more than that of one conductor of the Type FCC cable used in the installation.

324.101 Corrosion Resistance

Metal components of the system shall be either corrosion resistant, coated with corrosion-resistant materials, or insulated from contact with corrosive substances.

324.112 Insulation

The insulating material of the cable shall be moisture resistant and flame retardant. All insulating materials in the FCC systems shall be identified for their use.

324.120 Markings

(A) Cable Marking

Type FCC cable shall be clearly and durably marked on both sides at intervals of not more than 610 mm (24 in.) with the information required by 310.8(A) and with the following additional information:

Material of conductors

Maximum temperature rating

Ampacity

(B) Conductor Identification

Conductors shall be clearly and durably identified on both sides throughout their length as specified in 310.6.

Article 326 Integrated Gas Spacer Cable: Type IGS

Part I General

326.1 Scope

This article covers the use, installation, and construction specifications for integrated gas spacer cable, Type IGS.

326.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Integrated Gas Spacer Cable, Type IGS. A factory assembly of one or more conductors, each individually insulated and enclosed in a loose fit, nonmetallic flexible conduit as an integrated gas spacer cable rated 0 volts through 600 volts.

Part II Installation

326.10 Uses Permitted

Type IGS cable shall be permitted for use underground, including direct burial in the earth, as the following:

Service-entrance conductors

Feeder or branch-circuit conductors

Service conductors, underground

326.12 Uses Not Permitted

Type IGS cable shall not be used as interior wiring or be exposed in contact with buildings.

326.24 Bending Radius

Where the coilable nonmetallic conduit and cable are bent for installation purposes or are flexed or bent during shipment or installation, the radius of the curve of the inner edge measured to the inside of the bend shall not be less than specified in Table 326.24.

Table 326.24 Minimum Radii of Bends

Conduit Size Minimum Radii

Metric Designator Trade Size mm in.

53 2 600 24

78 3 900 35

103 4 1150 45

326.26 Bends

A run of Type IGS cable between pull boxes or terminations shall not contain more than the equivalent of four quarter bends (360 degrees total), including those bends located immediately at the pull box or terminations.

326.40 Fittings

Terminations and splices for Type IGS cable shall be identified as a type that is suitable for maintaining the gas pressure within the conduit. A valve and cap shall be provided for each length of the cable and conduit to check the gas pressure or to inject gas into the conduit.

326.80 Ampacity

The ampacity of Type IGS cable shall not exceed the values shown in Table 326.80.

Table 326.80 Ampacity of Type IGS Cable

Size (kcmil) Amperes Size (kcmil) Amperes

250 119 2500 376

500 168 3000 412

750 206 3250 429

1000 238 3500 445

1250 266 3750 461

1500 292 4000 476

1750 315 4250 491

2000 336 4500 505

2250 357 4750 519

Part III Construction Specifications

326.104 Conductors

The conductors shall be solid aluminum rods, laid parallel, consisting of one to nineteen 12.7 mm (1/2 in.) diameter rods. The minimum conductor size shall be 250 kcmil, and the maximum size shall be 4750 kcmil.

326.112 Insulation

The insulation shall be dry kraft paper tapes and a pressurized sulfur hexafluoride gas (SF6), both approved for electrical use. The nominal gas pressure shall be 138 kPa gauge (20 lb/in.2 gauge). The thickness of the paper spacer shall be as specified in Table 326.112.

Table 326.112 Paper Spacer Thickness

Thickness

Size (kcmil) mm in.

250—1000 1.02 0.040

1250—4750 1.52 0.060

326.116 Conduit

The conduit shall be a medium density polyethylene identified as suitable for use with natural gas rated pipe in metric designator 53, 78, or 103 (trade size 2, 3, or 4). The percent fill dimensions for the conduit are shown in Table 326.116.

The size of the conduit permitted for each conductor size shall be calculated for a percent fill not to exceed those found in Table 1, Chapter 9.

Table 326.116 Conduit Dimensions

Conduit Size Actual Outside

Diameter Actual Inside

Diameter

Metric Designator Trade Size mm in. mm in.

53 2 60 2.375 49.46 1.947

78 3 89 3.500 73.30 2.886

103 4 114 4.500 94.23 3.710

326.120 Marking

The cable shall be marked in accordance with 310.8(A), 310.8(B)(1), and 310.8(D).

Article 330 Metal-Clad Cable: Type MC

Part I General

330.1 Scope

This article covers the use, installation, and construction specifications of metal-clad cable, Type MC.

330.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Metal Clad Cable, Type MC. A factory assembly of one or more insulated circuit conductors with or without optical fiber members enclosed in an armor of interlocking metal tape, or a smooth or corrugated metallic sheath.

330.6 Listing Requirements

Type MC cable shall be listed. Fittings used for connecting Type MC cable to boxes, cabinets, or other equipment shall be listed and identified for such use.

Part II Installation

330.10 Uses Permitted

(A) General Uses

Type MC cable shall be permitted as follows:

For services, feeders, and branch circuits.

For power, lighting, control, and signal circuits.

Indoors or outdoors.

Exposed or concealed.

To be direct buried where identified for such use.

In cable tray where identified for such use.

In any raceway.

As aerial cable on a messenger.

In hazardous (classified) locations where specifically permitted by other articles in this Code.

In dry locations and embedded in plaster finish on brick or other masonry except in damp or wet locations.

In wet locations where a corrosion-resistant jacket is provided over the metallic covering and any of the following conditions are met:

The metallic covering is impervious to moisture.

A jacket resistant to moisture is provided under the metal covering.

The insulated conductors under the metallic covering are listed for use in wet locations.

Where single-conductor cables are used, all phase conductors and, where used, the grounded conductor shall be grouped together to minimize induced voltage on the sheath.

(B) Specific Uses

Type MC cable shall be permitted to be installed in compliance with Parts II and III of Article 725 and 770.133 as applicable and in accordance with 330.10(B)(1) through (B)(4).

Informational Note: The "Uses Permitted" is not an all-inclusive list.

(1) Cable Tray

Type MC cable installed in cable tray shall comply with 392.10, 392.12, 392.18, 392.20, 392.22, 392.30, 392.46, 392.56, 392.60(C), and 392.80.

(2) Direct Buried

Direct-buried cable shall comply with 300.5 or 300.50, as appropriate.

(3) Installed as Service-Entrance Cable

Type MC cable installed as service-entrance cable shall be permitted in accordance with 230.43.

(4) Installed Outside of Buildings or Structures or as Aerial Cable

Type MC cable installed outside of buildings or structures or as aerial cable shall comply with 225.10, 396.10, and 396.12.

330.12 Uses Not Permitted

Type MC cable shall not be used under either of the following conditions:

Where subject to physical damage

Where exposed to any of the destructive corrosive conditions in (a) or (b), unless the metallic sheath or armor is resistant to the conditions or is protected by material resistant to the conditions:

Direct buried in the earth or embedded in concrete unless identified for direct burial

Exposed to cinder fills, strong chlorides, caustic alkalis, or vapors of chlorine or of hydrochloric acids

330.15 Exposed Work

Exposed runs of cable, except as provided in 300.11(B), shall closely follow the surface of the building finish or of running boards. Exposed runs shall also be permitted to be installed on the underside of joists where supported at each joist and located so as not to be subject to physical damage.

330.17 Through or Parallel to Framing Members

Type MC cable shall be protected in accordance with 300.4(A), (C), and (D) where installed through or parallel to framing members.

330.23 In Accessible Attics

The installation of Type MC cable in accessible attics or roof spaces shall also comply with 320.23.

330.24 Bending Radius

Bends in Type MC cable shall be so made that the cable will not be damaged. The radius of the curve of the inner edge of any bend shall not be less than required in 330.24(A) through (C).

(A) Smooth Sheath

Ten times the external diameter of the metallic sheath for cable not more than 19 mm (3/4 in.) in external diameter

Twelve times the external diameter of the metallic sheath for cable more than 19 mm (3/4 in.) but not more than 38 mm (11/2 in.) in external diameter

Fifteen times the external diameter of the metallic sheath for cable more than 38 mm (11/2 in.) in external diameter

(B) Interlocked-Type Armor or Corrugated Sheath

Seven times the external diameter of the metallic sheath.

(C) Shielded Conductors

Twelve times the overall diameter of one of the individual conductors or seven times the overall diameter of the multiconductor cable, whichever is greater.

330.30 Securing and Supporting

(A) General

Type MC cable shall be supported and secured by staples; cable ties listed and identified for securement and support; straps, hangers, or similar fittings; or other approved means designed and installed so as not to damage the cable.

(B) Securing

Unless otherwise provided, cables shall be secured at intervals not exceeding 1.8 m (6 ft). Cables containing four or fewer conductors sized no larger than 10 AWG shall be secured within 300 mm (12 in.) of every box, cabinet, fitting, or other cable termination. In vertical installations, listed cables with ungrounded conductors 250 kcmil and larger shall be permitted to be secured at intervals not exceeding 3 m (10 ft).

(C) Supporting

Unless otherwise provided, cables shall be supported at intervals not exceeding 1.8 m (6 ft).

Horizontal runs of Type MC cable installed in wooden or metal framing members or similar supporting means shall be considered supported and secured where such support does not exceed 1.8-m (6-ft) intervals.

(D) Unsupported Cables

Type MC cable shall be permitted to be unsupported and unsecured where the cable complies with any of the following:

Is fished between access points through concealed spaces in finished buildings or structures and supporting is impractical.

Is not more than 1.8 m (6 ft) in length from the last point of cable support to the point of connection to luminaires or other electrical equipment and the cable and point of connection are within an accessible ceiling.

Is Type MC of the interlocked armor type in lengths not exceeding 900 mm (3 ft) from the last point where it is securely fastened and is used to connect equipment where flexibility is necessary to minimize the transmission of vibration from equipment or to provide flexibility for equipment that requires movement after installation.

For the purpose of this section, Type MC cable fittings shall be permitted as a means of cable support.

330.31 Single Conductors

Where single-conductor cables with a nonferrous armor or sheath are used, the installation shall comply with 300.20.

330.80 Ampacity

The ampacity of Type MC cable shall be determined in accordance with 310.14 or 311.60 for 14 AWG and larger conductors and in accordance with Table 402.5 for 18 AWG and 16 AWG conductors. The installation shall not exceed the temperature ratings of terminations and equipment.

(A) Type MC Cable Installed in Cable Tray

The ampacities for Type MC cable installed in cable tray shall be determined in accordance with 392.80.

(B) Single Type MC Conductors Grouped Together

Where single Type MC conductors are grouped together in a triangular or square configuration and installed on a messenger or exposed with a maintained free airspace of not less than 2.15 times one conductor diameter (2.15 × O.D.) of the largest conductor contained within the configuration and adjacent conductor configurations or cables, the ampacity of the conductors shall not exceed the allowable ampacities in the following tables:

Table 310.20 for conductors rated 0 volts through 2000 volts

Table 311.60(C)(67) and Table 311.60(C)(68) for conductors rated over 2000 volts

(C) Thermal Insulation

Where more than two Type MC cables containing two or more current-carrying conductors in each cable are installed in contact with thermal insulation, caulk, or sealing foam without maintaining spacing between cables, the ampacity of each conductor shall be adjusted in accordance with Table 310.15(C)(1).

Part III Construction Specifications

330.104 Conductors

For ungrounded, grounded, and equipment grounding conductors, the minimum conductor sizes shall be 14 AWG copper, nickel, or nickel-coated copper and 12 AWG aluminum or copper-clad aluminum.

For control and signal conductors minimum conductor sizes shall be 18 AWG copper, nickel, or nickel-coated copper, 14 AWG copper-clad aluminum, and 12 AWG aluminum.

330.108 Equipment Grounding Conductor

Where Type MC cable is used to provide an equipment grounding conductor, it shall comply with 250.118(10) and 250.122.

330.112 Insulation

Insulated conductors shall comply with 330.112(A) or (B).

(A) 1000 Volts or Less

Insulated conductors in sizes 18 AWG and 16 AWG shall be of a type listed in Table 402.3, with a maximum operating temperature not less than 90°C (194°F) and as permitted by 725.49. Conductors larger than 16 AWG shall be of a type listed in Table 310.4(A) or of a type identified for use in Type MC cable.

(B) Over 1000 Volts

Insulated conductors shall be of a type listed in Table 310.4(B) and Table 311.10(A).

330.116 Sheath

Metallic covering shall be one of the following types: smooth metallic sheath, corrugated metallic sheath, or interlocking metal tape armor. The metallic sheath shall be continuous and close fitting. A nonmagnetic sheath or armor shall be used on single conductor Type MC. Supplemental protection of an outer covering of corrosion-resistant material shall be permitted and shall be required where such protection is needed. The sheath shall not be used as a current-carrying conductor.

Informational Note: See 300.6 for protection against corrosion.

330.130 Hazardous (Classified) Locations

Where required to be marked MC-HL, the cable shall be listed and shall have a gas/vapor tight continuous corrugated metallic sheath, an overall jacket of suitable polymeric material, and a separate equipment grounding conductor.

Article 332 Mineral-Insulated, Metal-Sheathed Cable: Type MI

Part I General

332.1 Scope

This article covers the use, installation, and construction specifications for mineral-insulated, metal-sheathed cable, Type MI.

332.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Mineral-Insulated, Metal-Sheathed Cable, Type MI. A factory assembly of one or more conductors insulated with a highly compressed refractory mineral insulation and enclosed in a liquidtight and gastight continuous copper or alloy steel sheath.

332.6 Listing Requirements

Type MI cable and associated fittings shall be listed.

Part II Installation

332.10 Uses Permitted

Type MI cable shall be permitted as follows:

For services, feeders, and branch circuits

For power, lighting, control, and signal circuits

In dry, wet, or continuously moist locations

Indoors or outdoors

Where exposed or concealed

Where embedded in plaster, concrete, fill, or other masonry, whether above or below grade

In hazardous (classified) locations where specifically permitted by other articles in this Code

Where exposed to oil and gasoline

Where exposed to corrosive conditions not deteriorating to its sheath

In underground runs where suitably protected against physical damage and corrosive conditions

In or attached to cable tray

Informational Note: The "Uses Permitted" is not an all-inclusive list.

332.12 Uses Not Permitted

Type MI cable shall not be used under the following conditions or in the following locations:

In underground runs unless protected from physical damage, where necessary

Where exposed to conditions that are destructive and corrosive to the metallic sheath, unless additional protection is provided

332.17 Through or Parallel to Framing Members

Type MI cable shall be protected in accordance with 300.4 where installed through or parallel to framing members.

332.24 Bending Radius

Bends in Type MI cable shall be so made that the cable will not be damaged. The radius of the inner edge of any bend shall not be less than required as follows:

Five times the external diameter of the metallic sheath for cable not more than 19 mm (3/4 in.) in external diameter

Ten times the external diameter of the metallic sheath for cable greater than 19 mm (3/4 in.) but not more than 25 mm (1 in.) in external diameter

332.30 Securing and Supporting

Type MI cable shall be supported and secured by staples, straps, hangers, or similar fittings, designed and installed so as not to damage the cable, at intervals not exceeding 1.8 m (6 ft).

(A) Horizontal Runs Through Holes and Notches

In other than vertical runs, cables installed in accordance with 300.4 shall be considered supported and secured where such support does not exceed 1.8 m (6 ft) intervals.

(B) Unsupported Cable

Type MI cable shall be permitted to be unsupported where the cable is fished between access points through concealed spaces in finished buildings or structures and supporting is impracticable.

(C) Cable Trays

All MI cable installed in cable trays shall comply with 392.30(A).

332.31 Single Conductors

Where single-conductor cables are used, all phase conductors and, where used, the neutral conductor shall be grouped together to minimize induced voltage on the sheath.

332.40 Boxes and Fittings

(A) Fittings

Fittings used for connecting Type MI cable to boxes, cabinets, or other equipment shall be identified for such use.

(B) Terminal Seals

Where Type MI cable terminates, an end seal fitting shall be installed immediately after stripping to prevent the entrance of moisture into the insulation. The conductors extending beyond the sheath shall be individually provided with an insulating material.

332.80 Ampacity

The ampacity of Type MI cable shall be determined in accordance with 310.14. The conductor temperature at the end seal fitting shall not exceed the temperature rating of the listed end seal fitting, and the installation shall not exceed the temperature ratings of terminations or equipment.

(A) Type MI Cable Installed in Cable Tray

The ampacities for Type MI cable installed in cable tray shall be determined in accordance with 392.80(A).

(B) Single Type MI Conductors Grouped Together

Where single Type MI conductors are grouped together in a triangular or square configuration, as required by 332.31, and installed on a messenger or exposed with a maintained free air space of not less than 2.15 times one conductor diameter (2.15 × O.D.) of the largest conductor contained within the configuration and adjacent conductor configurations or cables, the ampacity of the conductors shall not exceed the allowable ampacities of Table 310.17.

Part III Construction Specifications

332.104 Conductors

Type MI cable conductors shall be of solid copper, nickel, or nickel-coated copper with a resistance corresponding to standard AWG and kcmil sizes.

332.108 Equipment Grounding Conductor

Where the outer sheath is made of copper, it shall provide an adequate path to serve as an equipment grounding conductor. Where the outer sheath is made of steel, a separate equipment grounding conductor shall be provided.

332.112 Insulation

The conductor insulation in Type MI cable shall be a highly compressed refractory mineral that provides proper spacing for all conductors.

332.116 Sheath

The outer sheath shall be of a continuous construction to provide mechanical protection and moisture seal.

Article 334 Nonmetallic-Sheathed Cable: Types NM and NMC

Part I General

334.1 Scope

This article covers the use, installation, and construction specifications of nonmetallic-sheathed cable.

334.2 Definitions

The definitions in this section shall apply within this article and throughout the Code.

Nonmetallic-Sheathed Cable. A factory assembly of two or more insulated conductors enclosed within an overall nonmetallic jacket.

Type NM. Insulated conductors enclosed within an overall nonmetallic jacket.

Type NMC. Insulated conductors enclosed within an overall, corrosion resistant, nonmetallic jacket.

334.6 Listing Requirements

Type NM and Type NMC cables and associated fittings shall be listed.

Part II Installation

334.10 Uses Permitted

Type NM and Type NMC cables shall be permitted to be used in the following, except as prohibited in 334.12:

One- and two-family dwellings and their attached or detached garages, and their storage buildings.

Multi-family dwellings permitted to be of Types III, IV, and V construction.

Other structures permitted to be of Types III, IV, and V construction. Cables shall be concealed within walls, floors, or ceilings that provide a thermal barrier of material that has at least a 15-minute finish rating as identified in listings of fire-rated assemblies.

Informational Note No. 1: Types of building construction and occupancy classifications are defined in NFPA 220-2018, Standard on Types of Building Construction, or the applicable building code, or both.

Informational Note No. 2: See Informative Annex E for determination of building types. [NFPA 220, Table 4.1.1]

Cable trays in structures permitted to be Types III, IV, or V where the cables are identified for the use.

Informational Note: See 310.14(A)(3) for temperature limitation of conductors.

Types I and II construction where installed within raceways permitted to be installed in Types I and II construction.

(A) Type NM

Type NM cable shall be permitted as follows:

For both exposed and concealed work in normally dry locations except as prohibited in 334.10(3)

To be installed or fished in air voids in masonry block or tile walls

(B) Type NMC

Type NMC cable shall be permitted as follows:

For both exposed and concealed work in dry, moist, damp, or corrosive locations, except as prohibited by 334.10(3)

In outside and inside walls of masonry block or tile

In a shallow chase in masonry, concrete, or adobe protected against nails or screws by a steel plate at least 1.59 mm (1/16 in.) thick and covered with plaster, adobe, or similar finish

334.12 Uses Not Permitted

(A) Types NM and NMC

Types NM and NMC cables shall not be permitted as follows:

In any dwelling or structure not specifically permitted in 334.10(1), (2), (3), and (5)

Exposed within a dropped or suspended ceiling cavity in other than one- and two-family and multifamily dwellings

As service-entrance cable

In commercial garages having hazardous (classified) locations as defined in 511.3

In theaters and similar locations, except where permitted in 518.4(B)

In motion picture studios

In storage battery rooms

In hoistways or on elevators or escalators

Embedded in poured cement, concrete, or aggregate

In hazardous (classified) locations, except where specifically permitted by other articles in this Code

(B) Type NM

Type NM cables shall not be used under the following conditions or in the following locations:

Where exposed to corrosive fumes or vapors

Where embedded in masonry, concrete, adobe, fill, or plaster

In a shallow chase in masonry, concrete, or adobe and covered with plaster, adobe, or similar finish

In wet or damp locations

334.15 Exposed Work

In exposed work, except as provided in 300.11(B), cable shall be installed as specified in 334.15(A) through (C).

(A) To Follow Surface

Cable shall closely follow the surface of the building finish or of running boards.

(B) Protection From Physical Damage

Cable shall be protected from physical damage where necessary by rigid metal conduit, intermediate metal conduit, electrical metallic tubing, Schedule 80 PVC conduit, Type RTRC marked with the suffix -XW, or other approved means. Where passing through a floor, the cable shall be enclosed in rigid metal conduit, intermediate metal conduit, electrical metallic tubing, Schedule 80 PVC conduit, Type RTRC marked with the suffix -XW, or other approved means extending at least 150 mm (6 in.) above the floor.

Type NMC cable installed in shallow chases or grooves in masonry, concrete, or adobe shall be protected in accordance with the requirements in 300.4(F) and covered with plaster, adobe, or similar finish.

(C) In Unfinished Basements and Crawl Spaces

Where cable is run at angles with joists in unfinished basements and crawl spaces, it shall be permissible to secure cables not smaller than two 6 AWG or three 8 AWG conductors directly to the lower edges of the joists. Smaller cables shall be run either through bored holes in joists or on running boards. Nonmetallic-sheathed cable installed on the wall of an unfinished basement shall be permitted to be installed in a listed conduit or tubing or shall be protected in accordance with 300.4. Conduit or tubing shall be provided with a suitable insulating bushing or adapter at the point the cable enters the raceway. The sheath of the nonmetallic-sheathed cable shall extend through the conduit or tubing and into the outlet or device box not less than 6 mm (1/4 in.). The cable shall be secured within 300 mm (12 in.) of the point where the cable enters the conduit or tubing. Metal conduit, tubing, and metal outlet boxes shall be connected to an equipment grounding conductor complying with the provisions of 250.86 and 250.148.

334.17 Through or Parallel to Framing Members

Types NM and NMC cable shall be protected in accordance with 300.4 where installed through or parallel to framing members. Grommets used as required in 300.4(B)(1) shall remain in place and be listed for the purpose of cable protection.

334.23 In Accessible Attics

The installation of cable in accessible attics or roof spaces shall also comply with 320.23.

334.24 Bending Radius

Bends in Types NM and NMC cable shall be so made that the cable will not be damaged. The radius of the curve of the inner edge of any bend during or after installation shall not be less than five times the diameter of the cable.

334.30 Securing and Supporting

Nonmetallic-sheathed cable shall be supported and secured by staples, cable ties listed and identified for securement and support, or straps, hangers, or similar fittings designed and installed so as not to damage the cable, at intervals not exceeding 1.4 m (41/2 ft) and within 300 mm (12 in.) of every cable entry into enclosures such as outlet boxes, junction boxes, cabinets, or fittings. The cable length between the cable entry and the closest cable support shall not exceed 450 mm (18 in.). Flat cables shall not be stapled on edge.

Sections of cable protected from physical damage by raceway shall not be required to be secured within the raceway.

(A) Horizontal Runs Through Holes and Notches

In other than vertical runs, cables installed in accordance with 300.4 shall be considered to be supported and secured where such support does not exceed 1.4-m (41/2-ft) intervals and the nonmetallic-sheathed cable is securely fastened in place by an approved means within 300 mm (12 in.) of each box, cabinet, conduit body, or other nonmetallic-sheathed cable termination.

Informational Note: See 314.17(B)(1) for support where nonmetallic boxes are used.

(B) Unsupported Cables

Nonmetallic-sheathed cable shall be permitted to be unsupported where the cable:

Is fished between access points through concealed spaces in finished buildings or structures and supporting is impracticable.

Is not more than 1.4 m (41/2 ft) from the last point of cable support to the point of connection to a luminaire or other piece of electrical equipment and the cable and point of connection are within an accessible ceiling in one-, two-, or multifamily dwellings.

(C) Wiring Device Without a Separate Outlet Box

A wiring device identified for the use, without a separate outlet box, and incorporating an integral cable clamp shall be permitted where the cable is secured in place at intervals not exceeding 1.4 m (41/2 ft) and within 300 mm (12 in.) from the wiring device wall opening, and there shall be at least a 300 mm (12 in.) loop of unbroken cable or 150 mm (6 in.) of a cable end available on the interior side of the finished wall to permit replacement.

334.40 Boxes and Fittings

(A) Boxes of Insulating Material

Nonmetallic outlet boxes shall be permitted as provided by 314.3.

(B) Devices of Insulating Material

Self-contained switches, self-contained receptacles, and nonmetallic-sheathed cable interconnector devices of insulating material that are listed shall be permitted to be used without boxes in exposed cable wiring and for repair wiring in existing buildings where the cable is concealed. Openings in such devices shall form a close fit around the outer covering of the cable, and the device shall fully enclose the part of the cable from which any part of the covering has been removed. Where connections to conductors are by binding-screw terminals, there shall be available as many terminals as conductors.

(C) Devices With Integral Enclosures

Wiring devices with integral enclosures identified for such use shall be permitted as provided by 300.15(E).

334.80 Ampacity

The ampacity of Types NM and NMC cable shall be determined in accordance with 310.14. The ampacity shall not exceed that of a 60°C (140°F) rated conductor. The 90°C (194°F) rating shall be permitted to be used for ampacity adjustment and correction calculations, provided the final calculated ampacity does not exceed that of a 60°C (140°F) rated conductor. The ampacity of Types NM and NMC cable installed in cable trays shall be determined in accordance with 392.80(A).

Where more than two NM cables containing two or more current-carrying conductors are installed, without maintaining spacing between the cables, through the same opening in wood framing that is to be sealed with thermal insulation, caulk, or sealing foam, the ampacity of each conductor shall be adjusted in accordance with Table 310.15(C)(1) and the provisions of 310.14(A)(2), Exception, shall not apply.

Where more than two NM cables containing two or more current-carrying conductors are installed in contact with thermal insulation without maintaining spacing between cables, the ampacity of each conductor shall be adjusted in accordance with Table 310.15(C)(1).

Part III Construction Specifications

334.100 Construction

The outer cable sheath of nonmetallic-sheathed cable shall be a nonmetallic material.

334.104 Conductors

The 600-volt insulated power conductors shall be sizes 14 AWG through 2 AWG copper conductors or sizes 12 AWG through 2 AWG aluminum or copper-clad aluminum conductors. Control and signaling conductors shall be no smaller than 18 AWG copper.

334.108 Equipment Grounding Conductor

In addition to the insulated conductors, the cable shall have an insulated, covered, or bare equipment grounding conductor.

334.112 Insulation

The insulated power conductors shall be one of the types listed in Table 310.4(A) that are suitable for branch-circuit wiring or one that is identified for use in these cables. Conductor insulation shall be rated at 90°C (194°F).

Informational Note: Types NM, NMC, and NMS cable identified by the markings NM-B, NMC-B, and NMS-B meet this requirement.

334.116 Sheath

The outer sheath of nonmetallic-sheathed cable shall comply with 334.116(A) and (B).

(A) Type NM

The overall covering shall be flame retardant and moisture resistant.

(B) Type NMC

The overall covering shall be flame retardant, moisture resistant, fungus resistant, and corrosion resistant.

Article 336 Power and Control Tray Cable: Type TC

Part I General

336.1 Scope

This article covers the use, installation, and construction specifications for power and control tray cable, Type TC.

336.2 Definition

The definition in this section shall apply within this article and throughout this Code.

Power and Control Tray Cable, Type TC. A factory assembly of two or more insulated conductors, with or without associated bare or covered equipment grounding conductors, under a nonmetallic jacket.

336.6 Listing Requirements

Type TC cables and associated fittings shall be listed.

Part II Installation

336.10 Uses Permitted

Type TC cable shall be permitted to be used as follows:

For power, lighting, control, and signal circuits.

In cable trays, including those with mechanically discontinuous segments up to 300 mm (1 ft).

In raceways.

In outdoor locations supported by a messenger wire.

For Class 1 circuits as permitted in Parts II and III of Article 725.

For non-power-limited fire alarm circuits if conductors comply with the requirements of 760.49.

Between a cable tray and the utilization equipment or device(s), provided all of the following apply:

The cable is Type TC-ER.

The cable is installed in industrial establishments where the conditions of maintenance and supervision ensure that only qualified persons service the installation.

The cable is continuously supported and protected against physical damage using mechanical protection such as struts, angles, or channels.

The cable complies with the crush and impact requirements of Type MC cable and is identified with the marking "TC-ER."

The cable is secured at intervals not exceeding 1.8 m (6 ft).

Equipment grounding for the utilization equipment is provided by an equipment grounding conductor within the cable. In cables containing conductors sized 6 AWG or smaller, the equipment grounding conductor shall be provided within the cable or, at the time of installation, one or more insulated conductors shall be permanently identified as an equipment grounding conductor in accordance with 250.119(B).

Exception to (7): Where not subject to physical damage, Type TC-ER shall be permitted to transition between cable trays and between cable trays and equipment or devices for a distance not to exceed 1.8 m (6 ft) without continuous support. The cable shall be mechanically supported where exiting the cable tray to ensure that the minimum bending radius is not exceeded.

Type TC cable shall be resistant to moisture and corrosive agents where installed in wet locations.

In one- and two-family dwelling units, Type TC-ER-JP cable containing both power and control conductors shall be permitted for branch circuits and feeders. Type TC-ER-JP cable used as interior wiring shall be installed per the requirements of Part II of Article 334 and where installed as exterior wiring shall be installed per the requirements of Part II of Article 340.

Exception: Where used to connect a generator and associated equipment having terminals rated 75°C (140°F) or higher, the cable shall not be limited in ampacity by 334.80 or 340.80.

Informational Note: See 725.136 for limitations on Class 2 or 3 circuits contained within the same cable with conductors of electric light, power, or Class 1 circuits.

Direct buried, where identified for such use.

In hazardous (classified) locations where specifically permitted by other articles in this Code.

Informational Note: See 310.14(A)(3) for temperature limitation of conductors.

336.12 Uses Not Permitted

Type TC tray cable shall not be installed or used as follows:

Installed where it will be exposed to physical damage

Installed outside a raceway or cable tray system, except as permitted in 336.10(4), 336.10(7), 336.10(9), and 336.10(10)

Used where exposed to direct rays of the sun, unless identified as sunlight resistant

336.24 Bending Radius

Bends in Type TC cable shall be made so as not to damage the cable. For Type TC cable without metal shielding, the minimum bending radius shall be as follows:

Four times the overall diameter for cables 25 mm (1 in.) or less in diameter

Five times the overall diameter for cables larger than 25 mm (1 in.) but not more than 50 mm (2 in.) in diameter

Six times the overall diameter for cables larger than 50 mm (2 in.) in diameter

Type TC cables with metallic shielding shall have a minimum bending radius of not less than 12 times the cable overall diameter.

336.80 Ampacity

The ampacity of Type TC tray cable shall be determined in accordance with 392.80(A) for 14 AWG and larger conductors, in accordance with 402.5 for 18 AWG through 16 AWG conductors where installed in cable trays, and in accordance with 310.14 where installed outside of cable trays, where permitted.

Part III Construction Specifications

336.100 Construction

A metallic sheath or armor as defined in 330.116 shall not be permitted either under or over the nonmetallic jacket. Metallic shield(s) shall be permitted over groups of conductors, under the outer jacket, or both.

336.104 Conductors

For ungrounded, grounded, and equipment grounding conductors, the conductor sizes shall be 14 AWG through 1000 kcmil copper, nickel, or nickel-coated copper and 12 AWG through 1000 kcmil aluminum or copper-clad aluminum. Insulation types shall be one of the types listed in Table 310.4(A) or Table 310.4(B) that is suitable for branch circuit and feeder circuits or one that is identified for such use.

For control and signal conductors, the minimum conductor sizes shall be 18 AWG copper, nickel, or nickel-coated copper, 14 AWG copper-clad aluminum, and 12 AWG aluminum.

(A) Fire Alarm Systems

Where used for fire alarm systems, conductors shall also be in accordance with 760.49.

(B) Thermocouple Circuits

Conductors in Type TC cable used for thermocouple circuits in accordance with Part III of Article 725 shall also be permitted to be any of the materials used for thermocouple extension wire.

(C) Class 1 Circuit Conductors

Insulated conductors of 18 AWG and 16 AWG copper shall also be in accordance with 725.49.

336.116 Jacket

The outer jacket shall be a flame-retardant, nonmetallic material.

336.120 Marking

There shall be no voltage marking on a Type TC cable employing thermocouple extension wire.

336.130 Hazardous (Classified) Location Cable

Cable listed and marked Type TC-ER-HL shall comply with the following:

The overall nonmetallic jacket shall be suitable for the environment.

The overall cable construction shall be essentially circular in cross-section.

The overall nonmetallic jacket shall be continuous and gas/vapor tight.

For construction greater than 25.4 mm (1 in.) in diameter, the following shall apply:

The equipment grounding conductor shall be bare.

A metallic shield shall be included over all conductors under the outer jacket.

Article 337 Type P Cable

Part I General

337.1 Scope

This article covers the use, installation, and construction specifications for up through 2000 volt Type P cable (armored and unarmored).

337.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Type P. Cable A factory assembly of one or more insulated flexible tinned copper conductors, with associated equipment grounding conductor(s), with or without a braided metallic armor and with an overall nonmetallic jacket.

337.6 Listing Requirements

Type P cables and associated fittings shall be listed.

Part II Installation

337.10 Uses Permitted

Type P cable shall be permitted to be used:

Under engineering supervision in industrial installations where conditions of maintenance and supervision ensure that only qualified persons monitor and service the system.

In hazardous (classified) locations where specifically permitted by other articles in this Code.

337.12 Uses Not Permitted

Type P cable shall not be installed or used:

Where it will be exposed to physical damage

Where not specifically permitted by other articles in the Code

337.24 Bending Radius

The minimum bending radii during installations and handling in service shall be adequate to prevent damage to the cable.

337.30 Securing and Supporting

Type P cable shall be supported and secured by cable ties listed and identified for securement and support; straps, hangers, or similar fittings; or other approved means designed and installed so as not to damage the cable.

337.31 Single Conductors

Where single-conductor cables are used, the installation shall comply with 300.20.

337.80 Ampacity

The ampacity of Type P cable shall be determined in accordance with 310.14(A) or 310.14(B) for 14 AWG and larger conductors. For 18 AWG and 16 AWG conductors the ampacities shall be determined in accordance with Table 402.5. When installed in cable tray, the ampacities shall be permitted to be determined in accordance with 392.80. The installation shall not exceed the temperature ratings of terminations and equipment.

Part III Construction Specifications

337.104 Conductors

Conductors shall be of tinned copper. Conductors shall employ flexible stranding. The minimum conductor size shall be 18 AWG.

337.108 Equipment Grounding Conductor

An equipment grounding conductor complying with 250.122 shall be provided within the cable.

337.112 Insulation

Insulated conductors shall be a thermoset type identified for use in Type P cable. All conductors shall be suitable for wet locations. The minimum wall thickness shall be 0.76 mm (30 mils).

337.114 Shield

Metallic shield(s) shall be permitted over a single conductor or groups of conductors.

337.115 Jacket

Single conductor cables and multiconductor cables shall have an overall nonmetallic jacket that is impervious to moisture, corrosion resistant, and sunlight resistant.

337.116 Armor

Armor shall be permitted over the jacket. If provided, the armor or metallic covering shall be a braided basket weave type consisting of wire laid closely together, flat and parallel, and forming a basket weave that shall firmly grip the cable. The wire shall be commercial bronze. The armor shall not be used as a current-carrying conductor or as an equipment grounding conductor. A nonmetallic jacket that conforms to 337.115 shall be provided over the armor.

337.120 Marking

Type P cable shall be marked in accordance with 310.8. When an armor is provided, the cable shall be marked accordingly.

Article 338 Service-Entrance Cable: Types SE and USE

Part I General

338.1 Scope

This article covers the use, installation, and construction specifications of service-entrance cable.

338.2 Definitions

The definition in this section shall apply within this article and throughout the Code.

Service-Entrance Cable. A single conductor or multiconductor cable provided with an overall covering, primarily used for services, and of the following types:

Type SE. Service-entrance cable having a flame-retardant, moisture-resistant covering.

Type USE. Service-entrance cable, identified for underground use, having a moisture-resistant covering, but not required to have a flame-retardant covering.

Service-Entrance Conductor Assembly. Multiple single-insulated conductors twisted together without an overall covering, other than an optional binder intended only to keep the conductors together.

338.6 Listing Requirements

Type SE and USE cables and associated fittings shall be listed.

Part II Installation

338.10 Uses Permitted

(A) Service-Entrance Conductors

Service-entrance cable shall be permitted to be used as service-entrance conductors and shall be installed in accordance with 230.6, 230.7, and Parts II, III, and IV of Article 230.

(B) Branch Circuits or Feeders

(1) Grounded Conductor Insulated

Type SE service-entrance cables shall be permitted in wiring systems where all of the circuit conductors of the cable are of the thermoset or thermoplastic type.

(2) Use of Uninsulated Conductor

Type SE service-entrance cable shall be permitted for use where the insulated conductors are used for circuit wiring and the uninsulated conductor is used only for equipment grounding purposes.

Exception: In existing installations, uninsulated conductors shall be permitted as a grounded conductor in accordance with 250.32 and 250.140, where the uninsulated grounded conductor of the cable originates in service equipment, and with 225.30 through 225.40.

(3) Temperature Limitations

Type SE service-entrance cable used to supply appliances shall not be subject to conductor temperatures in excess of the temperature specified for the type of insulation involved.

(4) Installation Methods for Branch Circuits and Feeders

Informational Note No. 1: See 310.14(A)(3) for temperature limitation of conductors.

Informational Note No. 2: For the installation of main power feeder conductors in dwelling units refer to 310.12.

(a) Interior Installations.

In addition to the provisions of this article, Type SE service-entrance cable used for interior wiring shall comply with the installation requirements of Part II of Article 334, excluding 334.80.

Where more than two Type SE cables containing two or more current-carrying conductors in each cable are installed in contact with thermal insulation, caulk, or sealing foam without maintaining spacing between cables, the ampacity of each conductor shall be adjusted in accordance with Table 310.15(C)(1).

For Type SE cable with ungrounded conductor sizes 10 AWG and smaller, where installed in contact with thermal insulation, the ampacity shall be in accordance with 60°C (140°F) conductor temperature rating. The maximum conductor temperature rating shall be permitted to be used for ampacity adjustment and correction purposes, if the final ampacity does not exceed that for a 60°C (140°F) rated conductor.

(b) Exterior Installations.

In addition to the provisions of this article, service-entrance cable used for feeders or branch circuits, where installed as exterior wiring, shall be installed in accordance with Part I of Article 225. The cable shall be supported in accordance with 334.30.

Type USE cable installed as underground feeder and branch circuit cable shall comply with Part II of Article 340.

Exception: Single-conductor Type USE and multi-rated USE conductors shall not be subject to the ampacity limitations of Part II of Article 340.

338.12 Uses Not Permitted

(A) Service-Entrance Cable

Service-entrance cable (SE) shall not be used under the following conditions or in the following locations:

Where subject to physical damage unless protected in accordance with 230.50(B)

Underground with or without a raceway

For exterior branch circuits and feeder wiring unless the installation complies with the provisions of Part I of Article 225 and is supported in accordance with 334.30 or is used as messenger-supported wiring as permitted in Part II of Article 396

(B) Underground Service-Entrance Cable

Underground service-entrance cable (USE) shall not be used under the following conditions or in the following locations:

For interior wiring

For aboveground installations except where USE cable emerges from the ground and is terminated in an enclosure at an outdoor location and the cable is protected in accordance with 300.5(D)

As aerial cable unless it is a multiconductor cable identified for use aboveground and installed as messenger-supported wiring in accordance with 225.10 and Part II of Article 396

338.24 Bending Radius

Bends in Types USE and SE cable shall be so made that the cable will not be damaged. The radius of the curve of the inner edge of any bend, during or after installation, shall not be less than five times the diameter of the cable.

Part III Construction Specifications

338.100 Construction

(A) Assemblies

Cabled assemblies of multiple single-conductor Type USE conductors shall be permitted for direct burial. All conductors shall be insulated.

Informational Note: The term "cabled" refers to a manufacturing process of twisting single conductors together and may also be referred to as "plexed."

(B) Uninsulated Conductor

Type SE or USE cable with an overall covering containing two or more conductors shall be permitted to have one conductor uninsulated.

338.120 Marking

Service-entrance cable shall be marked as required in 310.8. Cable with the neutral conductor smaller than the ungrounded conductors shall be so marked.

Article 340 Underground Feeder and Branch-Circuit Cable: Type UF

Part I General

340.1 Scope

This article covers the use, installation, and construction specifications for underground feeder and branch-circuit cable, Type UF.

340.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Underground Feeder and Branch-Circuit Cable, Type UF. A factory assembly of one or more insulated conductors with an integral or an overall covering of nonmetallic material suitable for direct burial in the earth.

340.6 Listing Requirements

Type UF cable and associated fittings shall be listed.

Part II Installation

340.10 Uses Permitted

Type UF cable shall be permitted as follows:

For use underground, including direct burial in the earth.

As single-conductor cables. Where installed as single-conductor cables, all conductors of the feeder or branch circuit, including the grounded conductor and equipment grounding conductor, if any, shall be installed in accordance with 300.3.

For wiring in wet, dry, or corrosive locations.

Installed as nonmetallic-sheathed cable. Where so installed, the installation and conductor requirements shall comply with Parts II and III of Article 334 and shall be of the multiconductor type.

As single-conductor cables as the nonheating leads for heating cables as provided in 424.43.

Supported by cable trays. Type UF cable supported by cable trays shall be of the multiconductor type.

Informational Note: See 310.14(A)(3) for temperature limitation of conductors.

340.12 Uses Not Permitted

Type UF cable shall not be used as follows:

As service-entrance cable

In commercial garages

In theaters and similar locations

In motion picture studios

In storage battery rooms

In hoistways or on elevators or escalators

In hazardous (classified) locations, except as specifically permitted by other articles in this Code

Embedded in poured cement, concrete, or aggregate, except where embedded in plaster as nonheating leads where permitted in 424.43

Where exposed to direct rays of the sun, unless identified as sunlight resistant

Informational Note: The sunlight-resistant marking on the jacket does not apply to the individual conductors.

Where subject to physical damage

As overhead cable, except where installed as messenger-supported wiring in accordance with Part II of Article 396

340.24 Bending Radius

Bends in Type UF cable shall be so made that the cable is not damaged. The radius of the curve of the inner edge of any bend shall not be less than five times the diameter of the cable.

340.80 Ampacity

The ampacity of Type UF cable shall be that of 60°C (140°F) conductors in accordance with 310.14.

Part III Construction Specifications

340.104 Conductors

The conductors shall be sizes 14 AWG copper or 12 AWG aluminum or copper-clad aluminum through 4/0 AWG.

340.108 Equipment Grounding Conductor

In addition to the insulated conductors, the cable shall be permitted to have an insulated or bare equipment grounding conductor.

340.112 Insulation

The conductors of Type UF shall be one of the moisture-resistant types listed in Table 310.4(A) that is suitable for branch-circuit wiring or one that is identified for such use. Where installed as a substitute wiring method for NM cable, the conductor insulation shall be rated 90°C (194°F).

340.116 Sheath

The overall covering shall be flame retardant; moisture, fungus, and corrosion resistant; and suitable for direct burial in the earth.

Article 342 Intermediate Metal Conduit: Type IMC

Part I General

342.1 Scope

This article covers the use, installation, and construction specifications for intermediate metal conduit (IMC) and associated fittings.

342.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Intermediate Metal Conduit (IMC). A steel threadable raceway of circular cross section designed for the physical protection and routing of conductors and cables and for use as an equipment grounding conductor when installed with its integral or associated coupling and appropriate fittings.

342.6 Listing Requirements

IMC, factory elbows and couplings, and associated fittings shall be listed.

Part II Installation

342.10 Uses Permitted

(A) All Atmospheric Conditions and Occupancies

Use of IMC shall be permitted under all atmospheric conditions and occupancies.

(B) Corrosion Environments

IMC, elbows, couplings, and fittings shall be permitted to be installed in concrete, in direct contact with the earth, or in areas subject to severe corrosive influences where protected by corrosion protection approved for the condition.

(C) Cinder Fill

IMC shall be permitted to be installed in or under cinder fill where subject to permanent moisture where protected on all sides by a layer of noncinder concrete not less than 50 mm (2 in.) thick; where the conduit is not less than 450 mm (18 in.) under the fill; or where protected by corrosion protection approved for the condition.

(D) Wet Locations

All supports, bolts, straps, screws, and so forth, shall be of corrosion-resistant materials or protected against corrosion by corrosion-resistant materials.

Informational Note: See 300.6 for protection against corrosion.

(E) Severe Physical Damage

IMC shall be permitted to be installed where subject to severe physical damage.

342.14 Dissimilar Metals

Where practicable, dissimilar metals in contact anywhere in the system shall be avoided to eliminate the possibility of galvanic action.

Stainless steel and aluminum fittings and enclosures shall be permitted to be used with galvanized steel IMC where not subject to severe corrosive influences.

Stainless steel IMC shall only be used with the following:

Stainless steel fittings

Stainless steel boxes and enclosures

Steel (galvanized, painted, powder or PVC coated, and so forth) boxes and enclosures when not subject to severe corrosive influences

Stainless steel, nonmetallic, or approved accessories

342.20 Size

(A) Minimum

IMC smaller than metric designator 16 (trade size 1/2) shall not be used.

(B) Maximum

IMC larger than metric designator 103 (trade size 4) shall not be used.

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

342.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

342.24 Bends — How Made

Bends of IMC shall be so made that the conduit will not be damaged and the internal diameter of the conduit will not be effectively reduced. The radius of the curve of any field bend to the centerline of the conduit shall not be less than indicated in Table 2, Chapter 9.

342.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

342.28 Reaming and Threading

All cut ends shall be reamed or otherwise finished to remove rough edges. Where conduit is threaded in the field, a standard cutting die with a taper of 1 in 16 (3/4 in. taper per foot) shall be used.

Informational Note: See ANSI/ASME B1.20.1-2013, Standard for Pipe Threads, General Purpose (Inch).

342.30 Securing and Supporting

IMC shall be installed as a complete system in accordance with 300.18 and shall be securely fastened in place and supported in accordance with 342.30(A) and (B).

(A) Securely Fastened

IMC shall be secured in accordance with one of the following:

IMC shall be securely fastened within 900 mm (3 ft) of each outlet box, junction box, device box, cabinet, conduit body, or other conduit termination.

Where structural members do not readily permit fastening within 900 mm (3 ft), fastening shall be permitted to be increased to a distance of 1.5 m (5 ft).

Where approved, conduit shall not be required to be securely fastened within 900 mm (3 ft) of the service head for above-the-roof termination of a mast.

(B) Supports

IMC shall be supported in accordance with one of the following:

Conduit shall be supported at intervals not exceeding 3 m (10 ft).

The distance between supports for straight runs of conduit shall be permitted in accordance with Table 344.30(B)(2), provided the conduit is made up with threaded couplings and supports that prevent transmission of stresses to termination where conduit is deflected between supports.

Exposed vertical risers from industrial machinery or fixed equipment shall be permitted to be supported at intervals not exceeding 6 m (20 ft) if the conduit is made up with threaded couplings, the conduit is supported and securely fastened at the top and bottom of the riser, and no other means of intermediate support is readily available.

Horizontal runs of IMC supported by openings through framing members at intervals not exceeding 3 m (10 ft) and securely fastened within 900 mm (3 ft) of termination points shall be permitted.

342.42 Couplings and Connectors

(A) Threadless

Threadless couplings and connectors used with conduit shall be made tight. Where buried in masonry or concrete, they shall be the concretetight type. Where installed in wet locations, they shall comply with 314.15. Threadless couplings and connectors shall not be used on threaded conduit ends unless listed for the purpose.

(B) Running Threads

Running threads shall not be used on conduit for connection at couplings.

342.46 Bushings

Where a conduit enters a box, fitting, or other enclosure, a bushing shall be provided to protect the wires from abrasion unless the box, fitting, or enclosure is designed to provide such protection.

Informational Note: See 300.4(G) for the protection of conductors 4 AWG and larger at bushings.

342.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

342.60 Grounding

IMC shall be permitted as an equipment grounding conductor.

Part III Construction Specifications

342.100 Construction

IMC shall be made of one of the following:

Steel, with protective coatings

Stainless steel

342.120 Marking

Each length shall be clearly and durably marked at least every 1.5 m (5 ft) with the letters IMC. Each length shall be marked as required in the first sentence of 110.21(A).

Article 344 Rigid Metal Conduit: Type RMC

Part I General

344.1 Scope

This article covers the use, installation, and construction specifications for rigid metal conduit (RMC) and associated fittings.

344.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Rigid Metal Conduit (RMC). A threadable raceway of circular cross section designed for the physical protection and routing of conductors and cables and for use as an equipment grounding conductor when installed with its integral or associated coupling and appropriate fittings.

344.6 Listing Requirements

RMC, factory elbows and couplings, and associated fittings shall be listed.

Part II Installation

344.10 Uses Permitted

(A) Atmospheric Conditions and Occupancies

(1) Galvanized Steel, Stainless Steel, and Red Brass RMC

Galvanized steel, stainless steel, and red brass RMC shall be permitted under all atmospheric conditions and occupancies.

(2) Aluminum RMC

Aluminum RMC shall be permitted to be installed where approved for the environment. Rigid aluminum conduit encased in concrete or in direct contact with the earth shall be provided with approved supplementary corrosion protection.

(3) Ferrous Raceways and Fittings

Ferrous raceways and fittings protected from corrosion solely by enamel shall be permitted only indoors and in occupancies not subject to severe corrosive influences.

(B) Corrosive Environments

(1) Galvanized Steel, Stainless Steel, and Red Brass RMC, Elbows, Couplings, and Fittings

Galvanized steel, stainless steel, and red brass RMC elbows, couplings, and fittings shall be permitted to be installed in concrete, in direct contact with the earth, or in areas subject to severe corrosive influences where protected by corrosion protection approved for the condition.

(2) Supplementary Protection of Aluminum RMC

Aluminum RMC shall be provided with approved supplementary corrosion protection where encased in concrete or in direct contact with the earth.

(C) Cinder Fill

Galvanized steel, stainless steel, and red brass RMC shall be permitted to be installed in or under cinder fill where subject to permanent moisture where protected on all sides by a layer of noncinder concrete not less than 50 mm (2 in.) thick; where the conduit is not less than 450 mm (18 in.) under the fill; or where protected by corrosion protection approved for the condition.

(D) Wet Locations

All supports, bolts, straps, screws, and so forth, shall be of corrosion-resistant materials or protected against corrosion by corrosion-resistant materials.

Informational Note: See 300.6 for protection against corrosion.

(E) Severe Physical Damage

RMC shall be permitted to be installed where subject to severe physical damage.

344.14 Dissimilar Metals

Where practicable, dissimilar metals in contact anywhere in the system shall be avoided to eliminate the possibility of galvanic action. Stainless steel and aluminum fittings and enclosures shall be permitted to be used with galvanized steel RMC, and galvanized steel fittings and enclosures shall be permitted to be used with aluminum RMC where not subject to severe corrosive influences. Stainless steel rigid conduit shall only be used with the following:

Stainless steel fittings

Stainless steel boxes and enclosures

Steel (galvanized, painted, powder or PVC coated, and so forth) boxes and enclosures when not subject to severe corrosive influences

Stainless steel, nonmetallic, or approved accessories

344.20 Size

(A) Minimum

RMC smaller than metric designator 16 (trade size 1/2) shall not be used.

Exception: For enclosing the leads of motors as permitted in 430.245(B).

(B) Maximum

RMC larger than metric designator 155 (trade size 6) shall not be used.

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

344.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

344.24 Bends — How Made

Bends of RMC shall be so made that the conduit will not be damaged and so that the internal diameter of the conduit will not be effectively reduced. The radius of the curve of any field bend to the centerline of the conduit shall not be less than indicated in Table 2, Chapter 9.

344.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

344.28 Reaming and Threading

All cut ends shall be reamed or otherwise finished to remove rough edges. Where conduit is threaded in the field, a standard cutting die with a 1 in 16 taper (3/4 in. taper per foot) shall be used.

Informational Note: See ANSI/ASME B1.20.1-2013, Standard for Pipe Threads, General Purpose (Inch).

344.30 Securing and Supporting

RMC shall be installed as a complete system in accordance with 300.18 and shall be securely fastened in place and supported in accordance with 344.30(A) and (B).

(A) Securely Fastened

RMC shall be secured in accordance with one of the following:

RMC shall be securely fastened within 900 mm (3 ft) of each outlet box, junction box, device box, cabinet, conduit body, or other conduit termination.

Fastening shall be permitted to be increased to a distance of 1.5 m (5 ft) where structural members do not readily permit fastening within 900 mm (3 ft).

Where approved, conduit shall not be required to be securely fastened within 900 mm (3 ft) of the service head for above-the-roof termination of a mast.

(B) Supports

RMC shall be supported in accordance with one of the following:

Conduit shall be supported at intervals not exceeding 3 m (10 ft).

The distance between supports for straight runs of conduit shall be permitted in accordance with Table 344.30(B)(2), provided the conduit is made up with threaded couplings and supports that prevent transmission of stresses to termination where conduit is deflected between supports.

Exposed vertical risers from industrial machinery or fixed equipment shall be permitted to be supported at intervals not exceeding 6 m (20 ft) if the conduit is made up with threaded couplings, the conduit is supported and securely fastened at the top and bottom of the riser, and no other means of intermediate support is readily available.

Horizontal runs of RMC supported by openings through framing members at intervals not exceeding 3 m (10 ft) and securely fastened within 900 mm (3 ft) of termination points shall be permitted.

Table 344.30(B)(2) Supports for Rigid Metal Conduit

Conduit Size Maximum Distance Between Rigid Metal Conduit Supports

Metric Designator Trade Size m ft

16—21 1/2—3/4 3.0 10

27 1 3.7 12

35—41 11/4—11/2 4.3 14

53—63 2—21/2 4.9 16

78 and larger 3 and larger 6.1 20

344.42 Couplings and Connectors

(A) Threadless

Threadless couplings and connectors used with conduit shall be made tight. Where buried in masonry or concrete, they shall be the concrete tight type. Where installed in wet locations, they shall comply with 314.15. Threadless couplings and connectors shall not be used on threaded conduit ends unless listed for the purpose.

(B) Running Threads

Running threads shall not be used on conduit for connection at couplings.

344.46 Bushings

Where a conduit enters a box, fitting, or other enclosure, a bushing shall be provided to protect the wires from abrasion unless the box, fitting, or enclosure is designed to provide such protection.

Informational Note: See 300.4(G) for the protection of conductors sizes 4 AWG and larger at bushings.

344.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

344.60 Grounding

RMC shall be permitted as an equipment grounding conductor.

Part III Construction Specifications

344.100 Construction

RMC shall be made of one of the following:

Steel with protective coatings

Aluminum

Red brass

Stainless steel

344.120 Marking

Each length shall be clearly and durably identified in every 3 m (10 ft) as required in the first sentence of 110.21(A). Nonferrous conduit of corrosion-resistant material shall have suitable markings.

Article 348 Flexible Metal Conduit: Type FMC

Part I General

348.1 Scope

This article covers the use, installation, and construction specifications for flexible metal conduit (FMC) and associated fittings.

348.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Flexible Metal Conduit (FMC). A raceway of circular cross section made of helically wound, formed, interlocked metal strip.

348.6 Listing Requirements

FMC and associated fittings shall be listed.

Part II Installation

348.10 Uses Permitted

FMC shall be permitted to be used in exposed and concealed locations.

348.12 Uses Not Permitted

FMC shall not be used in the following:

In wet locations

In hoistways, other than as permitted in 620.21(A)(1)

In storage battery rooms

In any hazardous (classified) location except as permitted by other articles in this Code

Where exposed to materials having a deteriorating effect on the installed conductors, such as oil or gasoline

Underground or embedded in poured concrete or aggregate

Where subject to physical damage

348.20 Size

(A) Minimum

FMC less than metric designator 16 (trade size 1/2) shall not be used unless permitted in 348.20(A)(1) through (A)(5) for metric designator 12 (trade size 3/8).

For enclosing the leads of motors as permitted in 430.245(B)

In lengths not in excess of 1.8 m (6 ft) for any of the following uses:

For utilization equipment

As part of a listed assembly

For tap connections to luminaires as permitted in 410.117(C)

For manufactured wiring systems as permitted in 604.100(A)

In hoistways as permitted in 620.21(A)(1)

As part of a listed assembly to connect wired luminaire sections as permitted in 410.137(C)

(B) Maximum

FMC larger than metric designator 103 (trade size 4) shall not be used.

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

348.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9, or as permitted in Table 348.22, or for metric designator 12 (trade size 3/8).

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

Table 348.22 Maximum Number of Insulated Conductors in Metric Designator 12 (Trade Size 3/8) Flexible Metal Conduit (FMC)\*

Size (AWG) Types RFH-2, SF-2 Types TF, XHHW, TW Types TFN, THHN, THWN Types FEP, FEBP, PF, PGF

Fittings Inside Conduit Fittings Outside Conduit Fittings Inside Conduit Fittings Outside Conduit Fittings Inside Conduit Fittings Outside Conduit Fittings Inside Conduit Fittings Outside Conduit

18 2 3 3 5 5 8 5 8

16 1 2 3 4 4 6 4 6

14 1 2 2 3 3 4 3 4

12 — — 1 2 2 3 2 3

10 — — 1 1 1 1 1 2

\*In addition, one insulated, covered, or bare equipment grounding conductor of the same size shall be permitted.

348.24 Bends — How Made

Bends in conduit shall be made so that the conduit is not damaged and the internal diameter of the conduit is not effectively reduced. Bends shall be permitted to be made manually without auxiliary equipment. The radius of the curve to the centerline of any bend shall not be less than shown in Table 2, Chapter 9 using the column "Other Bends."

348.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

348.28 Trimming

All cut ends shall be trimmed or otherwise finished to remove rough edges, except where fittings that thread into the convolutions are used.

348.30 Securing and Supporting

FMC shall be securely fastened in place and supported in accordance with 348.30(A) and (B).

(A) Securely Fastened

FMC shall be securely fastened in place by an approved means within 300 mm (12 in.) of each box, cabinet, conduit body, or other conduit termination and shall be supported and secured at intervals not to exceed 1.4 m (41/2 ft). Where used, cable ties shall be listed and be identified for securement and support.

Exception No. 1: Where FMC is fished between access points through concealed spaces in finished buildings or structures and supporting is impracticable.

Exception No. 2: Where flexibility is necessary after installation, lengths from the last point where the raceway is securely fastened shall not exceed the following:

900 mm (3 ft) for metric designators 16 through 35 (trade sizes 1/2 through 11/4)

1200 mm (4 ft) for metric designators 41 through 53 (trade sizes 11/2 through 2)

1500 mm (5 ft) for metric designators 63 (trade size 21/2) and larger

Exception No. 3: Lengths not exceeding 1.8 m (6 ft) from a luminaire terminal connection for tap connections to luminaires as permitted in 410.117(C).

Exception No. 4: Lengths not exceeding 1.8 m (6 ft) from the last point where the raceway is securely fastened for connections within an accessible ceiling to a luminaire(s) or other equipment. For the purposes of this exception, listed flexible metal conduit fittings shall be permitted as a means of securement and support.

(B) Supports

Horizontal runs of FMC supported by openings through framing members at intervals not greater than 1.4 m (41/2 ft) and securely fastened within 300 mm (12 in.) of termination points shall be permitted.

348.42 Couplings and Connectors

Angle connectors shall not be concealed.

348.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

348.60 Grounding and Bonding

If used to connect equipment where flexibility is necessary to minimize the transmission of vibration from equipment or to provide flexibility for equipment that requires movement after installation, an equipment grounding conductor shall be installed.

Where flexibility is not required after installation, FMC shall be permitted to be used as an equipment grounding conductor when installed in accordance with 250.118(5).

Where required or installed, equipment grounding conductors shall be installed in accordance with 250.134.

Where required or installed, equipment bonding jumpers shall be installed in accordance with 250.102.

Article 350 Liquidtight Flexible Metal Conduit: Type LFMC

Part I General

350.1 Scope

This article covers the use, installation, and construction specifications for liquidtight flexible metal conduit (LFMC) and associated fittings.

350.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Liquidtight Flexible Metal Conduit (LFMC). A raceway of circular cross section having an outer liquidtight, nonmetallic, sunlight-resistant jacket over an inner flexible metal core with associated couplings, connectors, and fittings for the installation of electric conductors.

350.6 Listing Requirements

LFMC and associated fittings shall be listed.

Part II Installation

350.10 Uses Permitted

LFMC shall be permitted to be used in exposed or concealed locations as follows:

Where conditions of installation, operation, or maintenance require flexibility or protection from machine oils, liquids, vapors, or solids.

In hazardous (classified) locations where specifically permitted by Chapter 5.

For direct burial where listed and marked for the purpose.

Conductors or cables rated at a temperature higher than the listed temperature rating of LFMC conduit shall be permitted to be installed in LFMC, provided the conductors or cables are not operated at a temperature higher than the listed temperature rating of the LFMC per 110.14(C).

350.12 Uses Not Permitted

LFMC shall not be used where subject to physical damage.

350.20 Size

(A) Minimum

LFMC smaller than metric designator 16 (trade size 1/2) shall not be used.

Exception: LFMC of metric designator 12 (trade size 3/8) shall be permitted as covered in 348.20(A).

(B) Maximum

The maximum size of LFMC shall be metric designator 103 (trade size 4).

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

350.22 Number of Conductors or Cables

(A) Metric Designators 16 through 103 (Trade Sizes 1/2 through 4)

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

(B) Metric Designator 12 (Trade Size 3/8)

The number of conductors shall not exceed that permitted in Table 348.22, "Fittings Outside Conduit" columns.

350.24 Bends — How Made

Bends in conduit shall be so made that the conduit will not be damaged and the internal diameter of the conduit will not be effectively reduced. Bends shall be permitted to be made manually without auxiliary equipment. The radius of the curve to the centerline of any bend shall not be less than required in Table 2, Chapter 9 using the column "Other Bends."

350.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

350.28 Trimming

All cut ends of conduit shall be trimmed inside and outside to remove rough edges.

350.30 Securing and Supporting

LFMC shall be securely fastened in place and supported in accordance with 350.30(A) and (B).

(A) Securely Fastened

LFMC shall be securely fastened in place by an approved means within 300 mm (12 in.) of each box, cabinet, conduit body, or other conduit termination and shall be supported and secured at intervals not to exceed 1.4 m (41/2 ft). Where used, cable ties shall be listed and be identified for securement and support.

Exception No. 1: Where LFMC is fished between access points through concealed spaces in finished buildings or structures and supporting is impractical.

Exception No. 2: Where flexibility is necessary after installation, lengths from the last point where the raceway is securely fastened shall not exceed the following:

900 mm (3 ft) for metric designators 16 through 35 (trade sizes (1/2 through 11/4)

1200 mm (4 ft) for metric designators 41 through 53 (trade sizes 11/2 through 2)

1500 mm (5 ft) for metric designators 63 (trade size 21/2) and larger

Exception No. 3: Lengths not exceeding 1.8 m (6 ft) from a luminaire terminal connection for tap conductors to luminaires, as permitted in 410.117(C).

Exception No. 4: Lengths not exceeding 1.8 m (6 ft) from the last point where the raceway is securely fastened for connections within an accessible ceiling to luminaire(s) or other equipment.

For the purposes of the exceptions, listed LFMC fittings shall be permitted as a means of securement and support.

(B) Supports

Horizontal runs of LFMC supported by openings through framing members at intervals not greater than 1.4 m (41/2 ft) and securely fastened within 300 mm (12 in.) of termination points shall be permitted.

350.42 Couplings and Connectors

Only fittings listed for use with LFMC shall be used. Angle connectors shall not be concealed. Straight LFMC fittings shall be permitted for direct burial where marked.

350.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

350.60 Grounding and Bonding

If used to connect equipment where flexibility is necessary to minimize the transmission of vibration from equipment or to provide flexibility for equipment that requires movement after installation, an equipment grounding conductor shall be installed.

Where flexibility is not required after installation, LFMC shall be permitted to be used as an equipment grounding conductor when installed in accordance with 250.118(6).

Where required or installed, equipment grounding conductors shall be installed in accordance with 250.134.

Where required or installed, equipment bonding jumpers shall be installed in accordance with 250.102.

Informational Note: See 501.30(B), 502.30(B), 503.30(B), 505.25(B), and 506.25(B) for types of equipment grounding conductors.

Part III Construction Specifications

350.120 Marking

LFMC shall be marked according to 110.21. The trade size and other information required by the listing shall also be marked on the conduit. Conduit suitable for direct burial shall be so marked.

Article 352 Rigid Polyvinyl Chloride Conduit: Type PVC

Part I General

352.1 Scope

This article covers the use, installation, and construction specifications for rigid polyvinyl chloride conduit (PVC) and associated fittings.

Informational Note: Refer to Article 353 for High Density Polyethylene Conduit: Type HDPE, and Article 355 for Reinforced Thermosetting Resin Conduit: Type RTRC.

352.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Rigid Polyvinyl Chloride Conduit (PVC). A rigid nonmetallic raceway of circular cross section, with integral or associated couplings, connectors, and fittings for the installation of electrical conductors and cables.

352.6 Listing Requirements

PVC conduit, factory elbows, and associated fittings shall be listed.

Part II Installation

352.10 Uses Permitted

The use of PVC conduit shall be permitted in accordance with 352.10(A) through (I).

Informational Note: Extreme cold may cause some nonmetallic conduits to become brittle and, therefore, more susceptible to damage from physical contact.

(A) Concealed

PVC conduit shall be permitted in walls, floors, and ceilings.

(B) Corrosive Influences

PVC conduit shall be permitted in locations subject to severe corrosive influences as covered in 300.6 and where subject to chemicals for which the materials are specifically approved.

(C) Cinders

PVC conduit shall be permitted in cinder fill.

(D) Wet Locations

PVC conduit shall be permitted in portions of dairies, laundries, canneries, or other wet locations, and in locations where walls are frequently washed, the entire conduit system, including boxes and fittings used therewith, shall be installed and equipped so as to prevent water from entering the conduit. All supports, bolts, straps, screws, and so forth, shall be of corrosion-resistant materials or be protected against corrosion by approved corrosion-resistant materials.

(E) Dry and Damp Locations

PVC conduit shall be permitted for use in dry and damp locations not prohibited by 352.12.

(F) Exposed

PVC conduit shall be permitted for exposed work. PVC conduit used exposed in areas of physical damage shall be identified for the use.

Informational Note: PVC Conduit, Type Schedule 80, is identified for areas of physical damage.

(G) Underground Installations

For underground installations, PVC shall be permitted for direct burial and underground encased in concrete. See 300.5 and 300.50.

(H) Support of Conduit Bodies

PVC conduit shall be permitted to support nonmetallic conduit bodies not larger than the largest trade size of an entering raceway. These conduit bodies shall not support luminaires or other equipment and shall not contain devices other than splicing devices as permitted by 110.14(B) and 314.16(C)(2).

(I) Insulation Temperature Limitations

Conductors or cables rated at a temperature higher than the listed temperature rating of PVC conduit shall be permitted to be installed in PVC conduit, provided the conductors or cables are not operated at a temperature higher than the listed temperature rating of the PVC conduit.

352.12 Uses Not Permitted

PVC conduit shall not be used under the conditions specified in 352.12(A) through (E).

(A) Hazardous (Classified) Locations

In any hazardous (classified) location, except as permitted by other articles of this Code.

(B) Support of Luminaires

For the support of luminaires or other equipment not described in 352.10(H).

(C) Physical Damage

Where subject to physical damage unless identified for such use.

(D) Ambient Temperatures

Where subject to ambient temperatures in excess of 50°C (122°F) unless listed otherwise.

(E) Theaters and Similar Locations

In theaters and similar locations, except as provided in 518.4 and 520.5.

352.20 Size

(A) Minimum

PVC conduit smaller than metric designator 16 (trade size 1/2) shall not be used.

(B) Maximum

PVC conduit larger than metric designator 155 (trade size 6) shall not be used.

Informational Note: The trade sizes and metric designators are for identification purposes only and do not relate to actual dimensions. See 300.1(C).

352.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

352.24 Bends — How Made

Bends shall be so made that the conduit will not be damaged and the internal diameter of the conduit will not be effectively reduced. Field bends shall be made only with identified bending equipment. The radius of the curve to the centerline of such bends shall not be less than shown in Table 2, Chapter 9.

352.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

352.28 Trimming

All cut ends shall be trimmed inside and outside to remove rough edges.

352.30 Securing and Supporting

PVC conduit shall be installed as a complete system as provided in 300.18 and shall be fastened so that movement from thermal expansion or contraction is permitted. PVC conduit shall be securely fastened and supported in accordance with 352.30(A) and (B).

Table 352.30 Support of Rigid Polyvinyl Chloride Conduit (PVC)

Conduit Size Maximum Spacing Between Supports

Metric Designator Trade Size mm or m ft

16—27 1/2—1 900 mm 3

35—53 11/4—2 1.5 m 5

63—78 21/2—3 1.8 m 6

91—129 31/2—5 2.1 m 7

155 6 2.5 m 8

(A) Securely Fastened

PVC conduit shall be securely fastened within 900 mm (3 ft) of each outlet box, junction box, device box, conduit body, or other conduit termination. Conduit listed for securing at other than 900 mm (3 ft) shall be permitted to be installed in accordance with the listing.

(B) Supports

PVC conduit shall be supported as required in Table 352.30. Conduit listed for support at spacings other than as shown in Table 352.30 shall be permitted to be installed in accordance with the listing. Horizontal runs of PVC conduit supported by openings through framing members at intervals not exceeding those in Table 352.30 and securely fastened within 900 mm (3 ft) of termination points shall be permitted.

352.44 Expansion Fittings

Expansion fittings for PVC conduit shall be provided to compensate for thermal expansion and contraction where the length change, in accordance with Table 352.44, is expected to be 6 mm (1/4 in.) or greater in a straight run between securely mounted items such as boxes, cabinets, elbows, or other conduit terminations.

Table 352.44 Expansion Characteristics of PVC Rigid Nonmetallic Conduit Coefficient of Thermal Expansion = 6.084 × 10—5 mm/mm/°C (3.38 × 10—5 in./in./°F)

Temperature Change (°C) Length Change of PVC Conduit (mm/m) Temperature Change (°F) Length Change of PVC Conduit (in./100 ft) Temperature Change (°F) Length Change of PVC Conduit (in./100 ft)

5 0.30 5 0.20 105 4.26

10 0.61 10 0.41 110 4.46

15 0.91 15 0.61 115 4.66

20 1.22 20 0.81 120 4.87

25 1.52 25 1.01 125 5.07

30 1.83 30 1.22 130 5.27

35 2.13 35 1.42 135 5.48

40 2.43 40 1.62 140 5.68

45 2.74 45 1.83 145 5.88

50 3.04 50 2.03 150 6.08

55 3.35 55 2.23 155 6.29

60 3.65 60 2.43 160 6.49

65 3.95 65 2.64 165 6.69

70 4.26 70 2.84 170 6.90

75 4.56 75 3.04 175 7.10

80 4.87 80 3.24 180 7.30

85 5.17 85 3.45 185 7.50

90 5.48 90 3.65 190 7.71

95 5.78 95 3.85 195 7.91

100 6.08 100 4.06 200 8.11

352.46 Bushings

Where a conduit enters a box, fitting, or other enclosure, a bushing or adapter shall be provided to protect the wire from abrasion unless the box, fitting, or enclosure design provides equivalent protection.

Informational Note: See 300.4(G) for the protection of conductors 4 AWG and larger at bushings.

352.48 Joints

All joints between lengths of conduit, and between conduit and couplings, fittings, and boxes, shall be made by an approved method.

352.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

352.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the conduit.

Exception No. 1: As permitted in 250.134, Exception No. 2, for dc circuits and 250.134, Exception No. 1, for separately run equipment grounding conductors.

Exception No. 2: Where the grounded conductor is used to ground equipment as permitted in 250.142.

Part III Construction Specifications

352.100 Construction

PVC conduit shall be made of rigid (nonplasticized) polyvinyl chloride (PVC). PVC conduit and fittings shall be composed of suitable nonmetallic material that is resistant to moisture and chemical atmospheres. For use aboveground, it shall also be flame retardant, resistant to impact and crushing, resistant to distortion from heat under conditions likely to be encountered in service, and resistant to low temperature and sunlight effects. For use underground, the material shall be acceptably resistant to moisture and corrosive agents and shall be of sufficient strength to withstand abuse, such as by impact and crushing, in handling and during installation. Where intended for direct burial, without encasement in concrete, the material shall also be capable of withstanding continued loading that is likely to be encountered after installation.

352.120 Marking

Each length of PVC conduit shall be clearly and durably marked at least every 3 m (10 ft) as required in the first sentence of 110.21(A). The type of material shall also be included in the marking unless it is visually identifiable. For conduit recognized for use aboveground, these markings shall be permanent. For conduit limited to underground use only, these markings shall be sufficiently durable to remain legible until the material is installed. Conduit shall be permitted to be surface marked to indicate special characteristics of the material.

Informational Note: Examples of these markings include but are not limited to "limited smoke" and "sunlight resistant."

Article 353 High Density Polyethylene Conduit: Type HDPE Conduit

Part I General

353.1 Scope

This article covers the use, installation, and construction specifications for high density polyethylene (HDPE) conduit and associated fittings.

Informational Note: Refer to Article 352 for Rigid Polyvinyl Chloride Conduit: Type PVC and Article 355 for Reinforced Thermosetting Resin Conduit: Type RTRC.

353.2 Definition

The definition in this section shall apply within this article and throughout the Code.

High Density Polyethylene (HDPE) Conduit. A nonmetallic raceway of circular cross section, with associated couplings, connectors, and fittings for the installation of electrical conductors.

353.6 Listing Requirements

HDPE conduit and associated fittings shall be listed.

Part II Installation

353.10 Uses Permitted

The use of HDPE conduit shall be permitted under the following conditions:

In discrete lengths or in continuous lengths from a reel

In locations subject to severe corrosive influences as covered in 300.6 and where subject to chemicals for which the conduit is listed

In cinder fill

In direct burial installations in earth or concrete

Informational Note to (4): Refer to 300.5 and 300.50 for underground installations.

Above ground, except as prohibited in 353.12, where encased in not less than 50 mm (2 in.) of concrete.

Conductors or cables rated at a temperature higher than the listed temperature rating of HDPE conduit shall be permitted to be installed in HDPE conduit, provided the conductors or cables are not operated at a temperature higher than the listed temperature rating of the HDPE conduit.

353.12 Uses Not Permitted

HDPE conduit shall not be used under the following conditions:

Where exposed

Within a building

In any hazardous (classified) location, except as permitted by other articles in this Code

Where subject to ambient temperatures in excess of 50°C (122°F) unless listed otherwise

353.20 Size

(A) Minimum

HDPE conduit smaller than metric designator 16 (trade size 1/2) shall not be used.

(B) Maximum

HDPE conduit larger than metric designator 155 (trade size 6) shall not be used.

Informational Note: The trade sizes and metric designators are for identification purposes only and do not relate to actual dimensions. See 300.1(C).

353.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

353.24 Bends — How Made

Bends shall be so made that the conduit will not be damaged and the internal diameter of the conduit will not be effectively reduced. Bends shall be permitted to be made manually without auxiliary equipment, and the radius of the curve to the centerline of such bends shall not be less than shown in Table 354.24. For conduits of metric designators 129 and 155 (trade sizes 5 and 6) the allowable radii of bends shall be in accordance with specifications provided by the manufacturer.

353.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

353.28 Trimming

All cut ends shall be trimmed inside and outside to remove rough edges.

353.46 Bushings

Where a conduit enters a box, fitting, or other enclosure, a bushing or adapter shall be provided to protect the wire from abrasion unless the box, fitting, or enclosure design provides equivalent protection.

Informational Note: See 300.4(G) for the protection of conductors 4 AWG and larger at bushings.

353.48 Joints

All joints between lengths of conduit, and between conduit and couplings, fittings, and boxes, shall be made by an approved method.

Informational Note: HDPE conduit can be joined using either heat fusion, electrofusion, or mechanical fittings.

353.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

353.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the conduit.

Exception No. 1: The equipment grounding conductor shall be permitted to be run separately from the conduit where used for grounding dc circuits as permitted in 250.134, Exception No. 2.

Exception No. 2: The equipment grounding conductor shall not be required where the grounded conductor is used to ground equipment as permitted in 250.142.

Part III Construction Specifications

353.100 Construction

HDPE conduit shall be composed of high density polyethylene that is resistant to moisture and chemical atmospheres. The material shall be resistant to moisture and corrosive agents and shall be of sufficient strength to withstand abuse, such as by impact and crushing, in handling and during installation. Where intended for direct burial, without encasement in concrete, the material shall also be capable of withstanding continued loading that is likely to be encountered after installation.

353.120 Marking

Each length of HDPE shall be clearly and durably marked at least every 3 m (10 ft) as required in 110.21. The type of material shall also be included in the marking.

Article 354 Nonmetallic Underground Conduit With Conductors: Type NUCC

Part I General

354.1 Scope

This article covers the use, installation, and construction specifications for nonmetallic underground conduit with conductors (NUCC).

354.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Nonmetallic Underground Conduit with Conductors (NUCC). A factory assembly of conductors or cables inside a nonmetallic, smooth wall raceway with a circular cross section.

354.6 Listing Requirements

NUCC and associated fittings shall be listed.

Part II Installation

354.10 Uses Permitted

The use of NUCC and fittings shall be permitted in the following:

For direct burial underground installation (For minimum cover requirements, see Table 300.5 and Table 300.50 under Rigid Nonmetallic Conduit.)

Encased or embedded in concrete

In cinder fill

In underground locations subject to severe corrosive influences as covered in 300.6 and where subject to chemicals for which the assembly is specifically approved

Aboveground, except as prohibited in 354.12, where encased in not less than 50 mm (2 in.) of concrete

354.12 Uses Not Permitted

NUCC shall not be used in the following:

In exposed locations

Inside buildings

Exception: The conductor or the cable portion of the assembly, where suitable, shall be permitted to extend within the building for termination purposes in accordance with 300.3.

In any hazardous (classified) location, except as permitted by other articles of this Code

354.20 Size

(A) Minimum

NUCC smaller than metric designator 16 (trade size 1/2) shall not be used.

(B) Maximum

NUCC larger than metric designator 103 (trade size 4) shall not be used.

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

354.22 Number of Conductors

The number of conductors or cables shall not exceed that permitted by the percentage fill in Table 1, Chapter 9.

354.24 Bends — How Made

Bends shall be manually made so that the conduit will not be damaged and the internal diameter of the conduit will not be effectively reduced. The radius of the curve of the centerline of such bends shall not be less than shown in Table 354.24.

Table 354.24 Minimum Bending Radius for Nonmetallic Underground Conduit with Conductors (NUCC)

Conduit Size Minimum Bending Radius

Metric Designator Trade Size mm in.

16 1/2 250 10

21 3/4 300 12

27 1 350 14

35 11/4 450 18

41 11/2 500 20

53 2 650 26

63 21/2 900 36

78 3 1200 48

103 4 1500 60

354.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between termination points.

354.28 Trimming

For termination, the conduit shall be trimmed away from the conductors or cables using an approved method that will not damage the conductor or cable insulation or jacket. All conduit ends shall be trimmed inside and out to remove rough edges.

354.46 Bushings

Where the NUCC enters a box, fitting, or other enclosure, a bushing or adapter shall be provided to protect the conductor or cable from abrasion unless the design of the box, fitting, or enclosure provides equivalent protection.

Informational Note: See 300.4(G) for the protection of conductors size 4 AWG or larger.

354.48 Joints

All joints between conduit, fittings, and boxes shall be made by an approved method.

354.50 Conductor Terminations

All terminations between the conductors or cables and equipment shall be made by an approved method for that type of conductor or cable.

354.56 Splices and Taps

Splices and taps shall be made in junction boxes or other enclosures.

354.60 Grounding

Where equipment grounding is required, an assembly containing a separate equipment grounding conductor shall be used.

Part III Construction Specifications

354.100 Construction

(A) General

NUCC is an assembly that is provided in continuous lengths shipped in a coil, reel, or carton.

(B) Nonmetallic Underground Conduit

The nonmetallic underground conduit shall be listed and composed of a material that is resistant to moisture and corrosive agents. It shall also be capable of being supplied on reels without damage or distortion and shall be of sufficient strength to withstand abuse, such as impact or crushing, in handling and during installation without damage to conduit or conductors.

(C) Conductors and Cables

Conductors and cables used in NUCC shall be listed and shall comply with 310.10(C). Conductors of different systems shall be installed in accordance with 300.3(C).

(D) Conductor Fill

The maximum number of conductors or cables in NUCC shall not exceed that permitted by the percentage fill in Table 1, Chapter 9.

354.120 Marking

NUCC shall be clearly and durably marked at least every 3.05 m (10 ft) as required by 110.21. The type of conduit material shall also be included in the marking.

Identification of conductors or cables used in the assembly shall be provided on a tag attached to each end of the assembly or to the side of a reel. Enclosed conductors or cables shall be marked in accordance with 310.8.

Article 355 Reinforced Thermosetting Resin Conduit: Type RTRC

Part I General

355.1 Scope

This article covers the use, installation, and construction specification for reinforced thermosetting resin conduit (RTRC) and associated fittings.

Informational Note: Refer to Article 352 for Rigid Polyvinyl Chloride Conduit: Type PVC, and Article 353 for High Density Polyethylene Conduit: Type HDPE.

355.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Reinforced Thermosetting Resin Conduit (RTRC). A rigid nonmetallic raceway of circular cross section, with integral or associated couplings, connectors, and fittings for the installation of electrical conductors and cables.

355.6 Listing Requirements

RTRC, factory elbows, and associated fittings shall be listed.

Part II Installation

355.10 Uses Permitted

The use of RTRC shall be permitted in accordance with 355.10(A) through (I).

(A) Concealed

RTRC shall be permitted in walls, floors, and ceilings.

(B) Corrosive Influences

RTRC shall be permitted in locations subject to severe corrosive influences as covered in 300.6 and where subject to chemicals for which the materials are specifically approved.

(C) Cinders

RTRC shall be permitted in cinder fill.

(D) Wet Locations

RTRC shall be permitted in portions of dairies, laundries, canneries, or other wet locations, and in locations where walls are frequently washed, the entire conduit system, including boxes and fittings used therewith, shall be installed and equipped so as to prevent water from entering the conduit. All supports, bolts, straps, screws, and so forth, shall be of corrosion-resistant materials or be protected against corrosion by approved corrosion-resistant materials.

(E) Dry and Damp Locations

RTRC shall be permitted for use in dry and damp locations not prohibited by 355.12.

(F) Exposed

RTRC shall be permitted for exposed work if identified for such use.

Informational Note: RTRC, Type XW, is identified for areas of physical damage.

(G) Underground Installations

For underground installations, see 300.5 and 300.50.

(H) Support of Conduit Bodies

RTRC shall be permitted to support nonmetallic conduit bodies not larger than the largest trade size of an entering raceway. These conduit bodies shall not support luminaires or other equipment and shall not contain devices other than splicing devices as permitted by 110.14(B) and 314.16(C)(2).

(I) Insulation Temperature Limitations

Conductors or cables rated at a temperature higher than the listed temperature rating of RTRC conduit shall be permitted to be installed in RTRC conduit, if the conductors or cables are not operated at a temperature higher than the listed temperature rating of the RTRC conduit.

355.12 Uses Not Permitted

RTRC shall not be used under the following conditions.

(A) Hazardous (Classified) Locations

In any hazardous (classified) location, except as permitted by other articles in this Code

In Class I, Division 2 locations, except as permitted in 501.10(B)(1)(6)

(B) Support of Luminaires

For the support of luminaires or other equipment not described in 355.10(H).

(C) Physical Damage

Where subject to physical damage unless identified for such use.

(D) Ambient Temperatures

Where subject to ambient temperatures in excess of 50°C (122°F) unless listed otherwise.

(E) Theaters and Similar Locations

In theaters and similar locations, except as provided in 518.4 and 520.5.

355.20 Size

(A) Minimum

RTRC smaller than metric designator 16 (trade size 1/2) shall not be used.

(B) Maximum

RTRC larger than metric designator 155 (trade size 6) shall not be used.

Informational Note: The trade sizes and metric designators are for identification purposes only and do not relate to actual dimensions. See 300.1(C).

355.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9. Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

355.24 Bends — How Made

Bends shall be so made that the conduit will not be damaged and the internal diameter of the conduit will not be effectively reduced. Field bends shall be made only with identified bending equipment. The radius of the curve to the centerline of such bends shall not be less than shown in Table 2, Chapter 9.

355.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

355.28 Trimming

All cut ends shall be trimmed inside and outside to remove rough edges.

355.30 Securing and Supporting

RTRC shall be installed as a complete system in accordance with 300.18 and shall be securely fastened in place and supported in accordance with 355.30(A) and (B).

Table 355.30 Support of Reinforced Thermosetting Resin Conduit (RTRC)

Conduit Size Maximum Spacing Between Supports

Metric Designator Trade Size mm or m ft

16—27 1/2—1 900 mm 3

35—53 11/4—2 1.5 m 5

63—78 21/2—3 1.8 m 6

91—129 31/2—5 2.1 m 7

155 6 2.5 m 8

(A) Securely Fastened

RTRC shall be securely fastened within 900 mm (3 ft) of each outlet box, junction box, device box, conduit body, or other conduit termination. Conduit listed for securing at other than 900 mm (3 ft) shall be permitted to be installed in accordance with the listing.

(B) Supports

RTRC shall be supported as required in Table 355.30. Conduit listed for support at spacing other than as shown in Table 355.30 shall be permitted to be installed in accordance with the listing. Horizontal runs of RTRC supported by openings through framing members at intervals not exceeding those in Table 355.30 and securely fastened within 900 mm (3 ft) of termination points shall be permitted.

355.44 Expansion Fittings

Expansion fittings for RTRC shall be provided to compensate for thermal expansion and contraction where the length change, in accordance with Table 355.44, is expected to be 6 mm (1/4 in.) or greater in a straight run between securely mounted items such as boxes, cabinets, elbows, or other conduit terminations.

Table 355.44 Expansion Characteristics of Reinforced Thermosetting Resin Conduit (RTRC) Coefficient of Thermal Expansion = 2.7 × 10—5 mm/mm/°C (1.5 × 10—5 in./in./°F)

Temperature Change (°C) Length Change of RTRC Conduit (mm/m) Temperature Change (°F) Length Change of RTRC Conduit (in./100 ft) Temperature Change (°F) Length Change of RTRC Conduit (in./100 ft)

5 0.14 5 0.09 105 1.89

10 0.27 10 0.18 110 1.98

15 0.41 15 0.27 115 2.07

20 0.54 20 0.36 120 2.16

25 0.68 25 0.45 125 2.25

30 0.81 30 0.54 130 2.34

35 0.95 35 0.63 135 2.43

40 1.08 40 0.72 140 2.52

45 1.22 45 0.81 145 2.61

50 1.35 50 0.90 150 2.70

55 1.49 55 0.99 155 2.79

60 1.62 60 1.08 160 2.88

65 1.76 65 1.17 165 2.97

70 1.89 70 1.26 170 3.06

75 2.03 75 1.35 175 3.15

80 2.16 80 1.44 180 3.24

85 2.30 85 1.53 185 3.33

90 2.43 90 1.62 190 3.42

95 2.57 95 1.71 195 3.51

100 2.70 100 1.80 200 3.60

355.46 Bushings

Where a conduit enters a box, fitting, or other enclosure, a bushing or adapter shall be provided to protect the wire from abrasion unless the box, fitting, or enclosure design provides equivalent protection.

Informational Note: See 300.4(G) for the protection of conductors 4 AWG and larger at bushings.

355.48 Joints

All joints between lengths of conduit, and between conduit and couplings, fitting, and boxes, shall be made by an approved method.

355.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

355.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the conduit.

Exception No. 1: As permitted in 250.134, Exception No. 2, for dc circuits and 250.134, Exception No. 1, for separately run equipment grounding conductors.

Exception No. 2: Where the grounded conductor is used to ground equipment as permitted in 250.142.

Part III Construction Specifications

355.100 Construction

RTRC and fittings shall be composed of suitable nonmetallic material that is resistant to moisture and chemical atmospheres. For use aboveground, it shall also be flame retardant, resistant to impact and crushing, resistant to distortion from heat under conditions likely to be encountered in service, and resistant to low temperature and sunlight effects. For use underground, the material shall be acceptably resistant to moisture and corrosive agents and shall be of sufficient strength to withstand abuse, such as by impact and crushing, in handling and during installation. Where intended for direct burial, without encasement in concrete, the material shall also be capable of withstanding continued loading that is likely to be encountered after installation.

355.120 Marking

Each length of RTRC shall be clearly and durably marked at least every 3 m (10 ft) as required in the first sentence of 110.21(A). The type of material shall also be included in the marking unless it is visually identifiable. For conduit recognized for use aboveground, these markings shall be permanent. For conduit limited to underground use only, these markings shall be sufficiently durable to remain legible until the material is installed. Conduit shall be permitted to be surface marked to indicate special characteristics of the material.

Informational Note: Examples of these markings include but are not limited to "limited smoke" and "sunlight resistant."

Article 356 Liquidtight Flexible Nonmetallic Conduit: Type LFNC

Part I General

356.1 Scope

This article covers the use, installation, and construction specifications for liquidtight flexible nonmetallic conduit (LFNC) and associated fittings.

356.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Liquidtight Flexible Nonmetallic Conduit (LFNC). A raceway of circular cross section of various types as follows:

A smooth seamless inner core and cover bonded together and having one or more reinforcement layers between the core and covers, designated as Type LFNC-A

A smooth inner surface with integral reinforcement within the raceway wall, designated as Type LFNC-B

A corrugated internal and external surface without integral reinforcement within the raceway wall, designated as Type LFNC-C

Informational Note: FNMC is an alternative designation for LFNC.

356.6 Listing Requirements

LFNC and associated fittings shall be listed.

Part II Installation

356.10 Uses Permitted

LFNC shall be permitted to be used in exposed or concealed locations for the following purposes:

Where flexibility is required for installation, operation, or maintenance.

Where protection of the contained conductors is required from vapors, machine oils, liquids, or solids.

For outdoor locations where listed and marked as suitable for the purpose.

For direct burial where listed and marked for the purpose.

Type LFNC shall be permitted to be installed in lengths longer than 1.8 m (6 ft) where secured in accordance with 356.30.

Type LFNC-B as a listed manufactured prewired assembly, metric designator 16 through 27 (trade size 1/2 through 1) conduit.

For encasement in concrete where listed for direct burial and installed in compliance with 356.42.

Conductors or cables rated at a temperature rating of LFNC conduit shall be permitted to be installed in LFNC, provided the conductors or cables are not operated at a temperature higher than the listed temperature rating of the LFNC.

Informational Note: Extreme cold can cause some types of nonmetallic conduits to become brittle and therefore more susceptible to damage from physical contact.

356.12 Uses Not Permitted

LFNC shall not be used as follows:

Where subject to physical damage

Where any combination of ambient and conductor temperatures is in excess of that for which it is listed

In lengths longer than 1.8 m (6 ft), except as permitted by 356.10(5) or where a longer length is approved as essential for a required degree of flexibility

In any hazardous (classified) location, except as permitted by other articles in this Code

356.20 Size

(A) Minimum

LFNC smaller than metric designator 16 (trade size 1/2) shall not be used unless permitted in 356.20(A)(1) or (A)(2) for metric designator 12 (trade size 3/8).

For enclosing the leads of motors as permitted in 430.245(B)

In lengths not exceeding 1.8 m (6 ft) as part of a listed assembly for tap connections to luminaires as required in 410.117(C), or for utilization equipment

(B) Maximum

LFNC larger than metric designator 103 (trade size 4) shall not be used.

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

356.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

356.24 Bends — How Made

Bends in conduit shall be so made that the conduit is not damaged and the internal diameter of the conduit is not effectively reduced. Bends shall be permitted to be made manually without auxiliary equipment. The radius of the curve to the centerline of any bend shall not be less than shown in Table 2, Chapter 9 using the column "Other Bends."

356.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

356.28 Trimming

All cut ends of conduit shall be trimmed inside and outside to remove rough edges.

356.30 Securing and Supporting

Type LFNC shall be securely fastened and supported in accordance with one of the following:

Where installed in lengths exceeding 1.8 m (6 ft), the conduit shall be securely fastened at intervals not exceeding 900 mm (3 ft) and within 300 mm (12 in.) on each side of every outlet box, junction box, cabinet, or fitting. Where used, cable ties shall be listed for the application and for securing and supporting.

Securing or supporting of the conduit shall not be required where it is fished, installed in lengths not exceeding 900 mm (3 ft) at terminals where flexibility is required, or installed in lengths not exceeding 1.8 m (6 ft) from a luminaire terminal connection for tap conductors to luminaires permitted in 410.117(C).

Horizontal runs of LFNC supported by openings through framing members at intervals not exceeding 900 mm (3 ft) and securely fastened within 300 mm (12 in.) of termination points shall be permitted.

Securing or supporting of LFNC shall not be required where installed in lengths not exceeding 1.8 m (6 ft) from the last point where the raceway is securely fastened for connections within an accessible ceiling to a luminaire(s) or other equipment. For the purpose of 356.30, listed liquidtight flexible nonmetallic conduit fittings shall be permitted as a means of support.

356.42 Couplings and Connectors

Only fittings listed for use with LFNC shall be used. Angle connectors shall not be used for concealed raceway installations. Straight LFNC fittings are permitted for direct burial or encasement in concrete.

356.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

356.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the conduit.

Exception No. 1: As permitted in 250.134, Exception No. 2, for dc circuits and 250.134, Exception No. 1, for separately run equipment grounding conductors.

Exception No. 2: Where the grounded conductor is used to ground equipment as permitted in 250.142.

Part III Construction Specifications

356.100 Construction

LFNC-B as a prewired manufactured assembly shall be provided in continuous lengths capable of being shipped in a coil, reel, or carton without damage.

356.120 Marking

LFNC shall be marked at least every 600 mm (2 ft) in accordance with 110.21. The marking shall include a type designation in accordance with 356.2 and the trade size. Conduit that is intended for outdoor use or direct burial shall be marked.

The type, size, and quantity of conductors used in prewired manufactured assemblies shall be identified by means of a printed tag or label attached to each end of the manufactured assembly and either the carton, coil, or reel. The enclosed conductors shall be marked in accordance with 310.8.

Article 358 Electrical Metallic Tubing: Type EMT

Part I General

358.1 Scope

This article covers the use, installation, and construction specifications for electrical metallic tubing (EMT) and associated fittings.

358.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Electrical Metallic Tubing (EMT). An unthreaded thinwall raceway of circular cross section designed for the physical protection and routing of conductors and cables and for use as an equipment grounding conductor when installed utilizing appropriate fittings.

358.6 Listing Requirements

EMT, factory elbows, and associated fittings shall be listed.

Part II Installation

358.10 Uses Permitted

(A) Exposed and Concealed

The use of EMT shall be permitted for both exposed and concealed work for the following:

In concrete, in direct contact with the earth or in areas subject to severe corrosive influences where installed in accordance with 358.10(B)

In dry, damp, and wet locations

In any hazardous (classified) location as permitted by other articles in this Code

(B) Corrosive Environments

(1) Galvanized Steel and Stainless Steel EMT, Elbows, and Fittings

Galvanized steel and stainless steel EMT, elbows, and fittings shall be permitted to be installed in concrete, in direct contact with the earth, or in areas subject to severe corrosive influences where protected by corrosion protection and approved as suitable for the condition.

(2) Supplementary Protection of Aluminum EMT

Aluminum EMT shall be provided with approved supplementary corrosion protection where encased in concrete or in direct contact with the earth.

(C) Cinder Fill

Galvanized steel and stainless steel EMT shall be permitted to be installed in cinder concrete or cinder fill where subject to permanent moisture when protected on all sides by a layer of noncinder concrete at least 50 mm (2 in.) thick or when the tubing is installed at least 450 mm (18 in.) under the fill.

(D) Wet Locations

All supports, bolts, straps, screws, and so forth shall be of corrosion-resistant materials or protected against corrosion by corrosion-resistant materials.

Informational Note: See 300.6 for protection against corrosion.

(E) Physical Damage

Steel and stainless steel EMT shall be permitted to be installed where subject to physical damage.

358.12 Uses Not Permitted

EMT shall not be used under the following conditions:

Where subject to severe physical damage

For the support of luminaires or other equipment except conduit bodies no larger than the largest trade size of the tubing

358.14 Dissimilar Metals

Where practicable, dissimilar metals in contact anywhere in the system shall be avoided to eliminate the possibility of galvanic action.

Stainless steel and aluminum fittings and enclosures shall be permitted to be used with galvanized steel EMT, and galvanized steel fittings and enclosures shall be permitted to be used with aluminum EMT where not subject to severe corrosive influences.

Stainless steel EMT shall only be used with the following:

Stainless steel fittings

Stainless steel boxes and enclosures

Steel (galvanized, painted, powder or PVC coated, and so forth) boxes and enclosures when not subject to severe corrosive influences

Stainless steel, nonmetallic, or approved accessories

358.20 Size

(A) Minimum

EMT smaller than metric designator 16 (trade size 1/2) shall not be used.

Exception: For enclosing the leads of motors as permitted in 430.245(B).

(B) Maximum

The maximum size of EMT shall be metric designator 103 (trade size 4).

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

358.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

358.24 Bends — How Made

Bends shall be made so that the tubing is not damaged and the internal diameter of the tubing is not effectively reduced. The radius of the curve of any field bend to the centerline of the tubing shall not be less than shown in Table 2, Chapter 9 for one-shot and full shoe benders.

358.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

358.28 Reaming and Threading

(A) Reaming

All cut ends of EMT shall be reamed or otherwise finished to remove rough edges.

(B) Threading

EMT shall not be threaded.

Exception: EMT with factory threaded integral couplings complying with 358.100.

358.30 Securing and Supporting

EMT shall be installed as a complete system in accordance with 300.18 and shall be securely fastened in place and supported in accordance with 358.30(A) and (B).

(A) Securely Fastened

EMT shall be securely fastened in place at intervals not to exceed 3 m (10 ft). In addition, each EMT run between termination points shall be securely fastened within 900 mm (3 ft) of each outlet box, junction box, device box, cabinet, conduit body, or other tubing termination.

Exception No. 1: Fastening of unbroken lengths shall be permitted to be increased to a distance of 1.5 m (5 ft) where structural members do not readily permit fastening within 900 mm (3 ft).

Exception No. 2: For concealed work in finished buildings or prefinished wall panels where such securing is impracticable, unbroken lengths (without coupling) of EMT shall be permitted to be fished.

(B) Supports

Horizontal runs of EMT supported by openings through framing members at intervals not greater than 3 m (10 ft) and securely fastened within 900 mm (3 ft) of termination points shall be permitted.

358.42 Couplings and Connectors

Couplings and connectors used with EMT shall be made up tight. Where buried in masonry or concrete, they shall be concretetight type. Where installed in wet locations, they shall comply with 314.15.

358.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

358.60 Grounding

EMT shall be permitted as an equipment grounding conductor.

Part III Construction Specifications

358.100 Construction

EMT shall be made of one of the following:

Steel with protective coatings

Aluminum

Stainless steel

358.120 Marking

EMT shall be clearly and durably marked at least every 3 m (10 ft) as required in the first sentence of 110.21(A).

Article 360 Flexible Metallic Tubing: Type FMT

Part I General

360.1 Scope

This article covers the use, installation, and construction specifications for flexible metallic tubing (FMT) and associated fittings.

360.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Flexible Metallic Tubing (FMT). A metal raceway that is circular in cross section, flexible, and liquidtight without a nonmetallic jacket.

360.6 Listing Requirements

FMT and associated fittings shall be listed.

Part II Installation

360.10 Uses Permitted

FMT shall be permitted to be used for branch circuits as follows:

In dry locations

Where concealed

In accessible locations

For system voltages of 1000 volts maximum

360.12 Uses Not Permitted

FMT shall not be used as follows:

In hoistways

In storage battery rooms

In hazardous (classified) locations unless otherwise permitted under other articles in this Code

Underground for direct earth burial, or embedded in poured concrete or aggregate

Where subject to physical damage

In lengths over 1.8 m (6 ft)

360.20 Size

(A) Minimum

FMT smaller than metric designator 16 (trade size 1/2) shall not be used.

Exception No. 1: FMT of metric designator 12 (trade size 3/8) shall be permitted to be installed in accordance with 300.22(B) and (C).

Exception No. 2: FMT of metric designator 12 (trade size 3/8) shall be permitted in lengths not in excess of 1.8 m (6 ft) as part of a listed assembly or for luminaires. See 410.117(C).

(B) Maximum

The maximum size of FMT shall be metric designator 21 (trade size 3/4).

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

360.22 Number of Conductors

(A) FMT — Metric Designators 16 and 21 (Trade Sizes 1/2 and 3/4)

The number of conductors in metric designators 16 (trade size 1/2) and 21 (trade size 3/4) shall not exceed that permitted by the percentage fill specified in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

(B) FMT — Metric Designator 12 (Trade Size 3/8)

The number of conductors in metric designator 12 (trade size 3/8) shall not exceed that permitted in Table 348.22.

360.24 Bends

(A) Infrequent Flexing Use

When FMT is infrequently flexed in service after installation, the radii of bends measured to the inside of the bend shall not be less than specified in Table 360.24(A).

Table 360.24(A) Minimum Radii for Flexing Use

Minimum Radii for Flexing Use

Metric Designator Trade Size mm in.

12 3/8 254.0 10

16 1/2 317.5 121/2

21 3/4 444.5 171/2

(B) Fixed Bends

Where FMT is bent for installation purposes and is not flexed or bent as required by use after installation, the radii of bends measured to the inside of the bend shall not be less than specified in Table 360.24(B).

Table 360.24(B) Minimum Radii for Fixed Bends

Minimum Radii for Fixed Bends

Metric Designator Trade Size mm in.

12 3/8 88.9 31/2

16 1/2 101.6 4

21 3/4 127.0 5

360.56 Splices and Taps

Splices and taps shall be made in accordance with 300.15.

360.60 Grounding

FMT shall be permitted as an equipment grounding conductor where installed in accordance with 250.118(7).

Part III Construction Specifications

360.120 Marking

FMT shall be marked according to 110.21.

Article 362 Electrical Nonmetallic Tubing: Type ENT

Part I General

362.1 Scope

This article covers the use, installation, and construction specifications for electrical nonmetallic tubing (ENT) and associated fittings.

362.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Electrical Nonmetallic Tubing (ENT). A nonmetallic, pliable, corrugated raceway of circular cross section with integral or associated couplings, connectors, and fittings for the installation of electrical conductors. ENT is composed of a material that is resistant to moisture and chemical atmospheres and is flame retardant.

A pliable raceway is a raceway that can be bent by hand with a reasonable force but without other assistance.

362.6 Listing Requirements

ENT and associated fittings shall be listed.

Part II Installation

362.10 Uses Permitted

For the purpose of this article, the first floor of a building shall be that floor that has 50 percent or more of the exterior wall surface area level with or above finished grade. One additional level that is the first level and not designed for human habitation and used only for vehicle parking, storage, or similar use shall be permitted. The use of ENT and fittings shall be permitted in the following:

In any building not exceeding three floors above grade as follows:

For exposed work, where not prohibited by 362.12

Concealed within walls, floors, and ceilings

In any building exceeding three floors above grade, ENT shall be concealed within walls, floors, and ceilings where the walls, floors, and ceilings provide a thermal barrier of material that has at least a 15-minute finish rating as identified in listings of fire-rated assemblies. The 15-minute-finish-rated thermal barrier shall be permitted to be used for combustible or noncombustible walls, floors, and ceilings.

Exception to (2): Where a fire sprinkler system(s) is installed in accordance with NFPA 13-2016, Standard for the Installation of Sprinkler Systems, on all floors, ENT shall be permitted to be used within walls, floors, and ceilings, exposed or concealed, in buildings exceeding three floors abovegrade.

Informational Note: A finish rating is established for assemblies containing combustible (wood) supports. The finish rating is defined as the time at which the wood stud or wood joist reaches an average temperature rise of 121°C (250°F) or an individual temperature of 163°C (325°F) as measured on the plane of the wood nearest the fire. A finish rating is not intended to represent a rating for a membrane ceiling.

In locations subject to severe corrosive influences as covered in 300.6 and where subject to chemicals for which the materials are specifically approved.

In concealed, dry, and damp locations not prohibited by 362.12.

Above suspended ceilings where the suspended ceilings provide a thermal barrier of material that has at least a 15-minute finish rating as identified in listings of fire-rated assemblies, except as permitted in 362.10(1)a.

Exception to (5): ENT shall be permitted to be used above suspended ceilings in buildings exceeding three floors above grade where the building is protected throughout by a fire sprinkler system installed in accordance with NFPA 13-2016, Standard for the Installation of Sprinkler Systems.

Encased in poured concrete, or embedded in a concrete slab on grade where ENT is placed on sand or approved screenings, provided fittings identified for this purpose are used for connections.

For wet locations indoors as permitted in this section or in a concrete slab on or belowgrade, with fittings listed for the purpose.

Metric designator 16 through 27 (trade size 1/2 through 1) as listed manufactured prewired assembly.

Conductors or cables rated at a temperature higher than the listed temperature rating of ENT shall be permitted to be installed in ENT, if the conductors or cables are not operated at a temperature higher than the listed temperature rating of the ENT.

362.12 Uses Not Permitted

ENT shall not be used in the following:

In any hazardous (classified) location, except as permitted by other articles in this Code

For the support of luminaires and other equipment

Where subject to ambient temperatures in excess of 50°C (122°F) unless listed otherwise

For direct earth burial

In exposed locations, except as permitted by 362.10(1), 362.10(5), and 362.10(7)

In theaters and similar locations, except as provided in 518.4 and 520.5

Where exposed to the direct rays of the sun, unless identified as sunlight resistant

Where subject to physical damage

Informational Note: Extreme cold may cause some types of nonmetallic conduits to become brittle and therefore more susceptible to damage from physical contact.

362.20 Size

(A) Minimum

ENT smaller than metric designator 16 (trade size 1/2) shall not be used.

(B) Maximum

ENT larger than metric designator 63 (trade size 21/2) shall not be used.

Informational Note: See 300.1(C) for the metric designators and trade sizes. These are for identification purposes only and do not relate to actual dimensions.

362.22 Number of Conductors

The number of conductors shall not exceed that permitted by the percentage fill in Table 1, Chapter 9.

Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles. The number of cables shall not exceed the allowable percentage fill specified in Table 1, Chapter 9.

362.24 Bends — How Made

Bends shall be so made that the tubing will not be damaged and the internal diameter of the tubing will not be effectively reduced. Bends shall be permitted to be made manually without auxiliary equipment, and the radius of the curve to the centerline of such bends shall not be less than shown in Table 2, Chapter 9 using the column "Other Bends."

362.26 Bends — Number in One Run

There shall not be more than the equivalent of four quarter bends (360 degrees total) between pull points, for example, conduit bodies and boxes.

362.28 Trimming

All cut ends shall be trimmed inside and outside to remove rough edges.

362.30 Securing and Supporting

ENT shall be installed as a complete system in accordance with 300.18 and shall be securely fastened in place by an approved means and supported in accordance with 362.30(A) and (B).

(A) Securely Fastened

ENT shall be securely fastened at intervals not exceeding 900 mm (3 ft). In addition, ENT shall be securely fastened in place within 900 mm (3 ft) of each outlet box, device box, junction box, cabinet, or fitting where it terminates. Where used, cable ties shall be listed for the application and for securing and supporting.

Exception No. 1: Lengths not exceeding a distance of 1.8 m (6 ft) from a luminaire terminal connection for tap connections to lighting luminaires shall be permitted without being secured.

Exception No. 2: Lengths not exceeding 1.8 m (6 ft) from the last point where the raceway is securely fastened for connections within an accessible ceiling to luminaire(s) or other equipment.

Exception No. 3: For concealed work in finished buildings or prefinished wall panels where such securing is impracticable, unbroken lengths (without coupling) of ENT shall be permitted to be fished.

(B) Supports

Horizontal runs of ENT supported by openings in framing members at intervals not exceeding 900 mm (3 ft) and securely fastened within 900 mm (3 ft) of termination points shall be permitted.

362.46 Bushings

Where a tubing enters a box, fitting, or other enclosure, a bushing or adapter shall be provided to protect the wire from abrasion unless the box, fitting, or enclosure design provides equivalent protection.

Informational Note: See 300.4(G) for the protection of conductors size 4 AWG or larger.

362.48 Joints

All joints between lengths of tubing and between tubing and couplings, fittings, and boxes shall be by an approved method.

362.56 Splices and Taps

Splices and taps shall be made only in accordance with 300.15.

Informational Note: See Article 314 for rules on the installation and use of boxes and conduit bodies.

362.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the raceway in compliance with Article 250, Part VI.

Part III Construction Specifications

362.100 Construction

ENT shall be made of material that does not exceed the ignitibility, flammability, smoke generation, and toxicity characteristics of rigid (nonplasticized) polyvinyl chloride.

ENT, as a prewired manufactured assembly, shall be provided in continuous lengths capable of being shipped in a coil, reel, or carton without damage.

362.120 Marking

ENT shall be clearly and durably marked at least every 3 m (10 ft) as required in the first sentence of 110.21(A). The type of material shall also be included in the marking. Marking for limited smoke shall be permitted on the tubing that has limited smoke-producing characteristics.

The type, size, and quantity of conductors used in prewired manufactured assemblies shall be identified by means of a printed tag or label attached to each end of the manufactured assembly and either the carton, coil, or reel. The enclosed conductors shall be marked in accordance with 310.8.

Article 366 Auxiliary Gutters

Part I General

366.1 Scope

This article covers the use, installation, and construction requirements of metal auxiliary gutters and nonmetallic auxiliary gutters and associated fittings.

366.2 Definitions

The definitions in this section shall apply within this article and throughout the Code.

Metal Auxiliary Gutter. A sheet metal enclosure used to supplement wiring spaces at meter centers, distribution centers, switchgear, switchboards, and similar points of wiring systems. The enclosure has hinged or removable covers for housing and protecting electrical wires, cable, and busbars. The enclosure is designed for conductors to be laid or set in place after the enclosures have been installed as a complete system.

Nonmetallic Auxiliary Gutter. A flame-retardant, nonmetallic enclosure used to supplement wiring spaces at meter centers, distribution centers, switchgear, switchboards, and similar points of wiring systems. The enclosure has hinged or removable covers for housing and protecting electrical wires, cable, and busbars. The enclosure is designed for conductors to be laid or set in place after the enclosures have been installed as a complete system.

366.6 Listing Requirements

(A) Outdoors

Nonmetallic auxiliary gutters installed outdoors shall be listed for all of the following conditions:

Exposure to sunlight

Use in wet locations

Maximum ambient temperature of the installation

(B) Indoors

Nonmetallic auxiliary gutters installed indoors shall be listed for the maximum ambient temperature of the installation.

Part II Installation

366.10 Uses Permitted

(A) Sheet Metal Auxiliary Gutters

(1) Indoor and Outdoor Use

Sheet metal auxiliary gutters shall be permitted for indoor and outdoor use.

(2) Wet Locations

Sheet metal auxiliary gutters installed in wet locations shall be suitable for such locations.

(B) Nonmetallic Auxiliary Gutters

Nonmetallic auxiliary gutters shall be listed for the maximum ambient temperature of the installation and marked for the installed conductor insulation temperature rating.

Informational Note: Extreme cold may cause nonmetallic auxiliary gutters to become brittle and therefore more susceptible to damage from physical contact.

(1) Outdoors

Nonmetallic auxiliary gutters shall be permitted to be installed outdoors where listed and marked as suitable for the purpose.

(2) Indoors

Nonmetallic auxiliary gutters shall be permitted to be installed indoors.

366.12 Uses Not Permitted

Auxiliary gutters shall not be used:

To enclose switches, overcurrent devices, appliances, or other similar equipment

To extend a greater distance than 9 m (30 ft) beyond the equipment that it supplements

Exception: As permitted in 620.35 for elevators, an auxiliary gutter shall be permitted to extend a distance greater than 9 m (30 ft) beyond the equipment it supplements.

Informational Note: For wireways, see Articles 376 and 378. For busways, see Article 368.

366.20 Conductors Connected in Parallel

Where single conductor cables comprising each phase, neutral, or grounded conductor of an alternating-current circuit are connected in parallel as permitted in 310.10(G), the conductors shall be installed in groups consisting of not more than one conductor per phase, neutral, or grounded conductor to prevent current imbalance in the paralleled conductors due to inductive reactance.

366.22 Number of Conductors

(A) Sheet Metal Auxiliary Gutters

The sum of the cross-sectional areas of all contained conductors and cables at any cross section of a sheet metal auxiliary gutter shall not exceed 20 percent of the interior cross-sectional area of the sheet metal auxiliary gutter.

(B) Nonmetallic Auxiliary Gutters

The sum of cross-sectional areas of all contained conductors and cables at any cross section of the nonmetallic auxiliary gutter shall not exceed 20 percent of the interior cross-sectional area of the nonmetallic auxiliary gutter.

366.23 Ampacity of Conductors

(A) Sheet Metal Auxiliary Gutters

The adjustment factors in 310.15(C)(1) shall be applied only where the number of current-carrying conductors, including neutral conductors classified as current-carrying under 310.15(E), exceeds 30 at any cross section of the sheet metal auxiliary gutter. Conductors for signaling circuits or controller conductors between a motor and its starter and used only for starting duty shall not be considered as current-carrying conductors. The current carried continuously in bare copper bars in sheet metal auxiliary gutters shall not exceed 1.55 amperes/mm2 (1000 amperes/in.2) of cross section of the conductor. For aluminum bars, the current carried continuously shall not exceed 1.09 amperes/mm2 (700 amperes/in.2) of cross section of the conductor.

(B) Nonmetallic Auxiliary Gutters

The adjustment factors specified in 310.15(C)(1) shall be applicable to the current-carrying conductors up to and including the 20 percent fill specified in 366.22(B).

366.30 Securing and Supporting

(A) Sheet Metal Auxiliary Gutters

Sheet metal auxiliary gutters shall be supported and secured throughout their entire length at intervals not exceeding 1.5 m (5 ft).

(B) Nonmetallic Auxiliary Gutters

Nonmetallic auxiliary gutters shall be supported and secured at intervals not to exceed 900 mm (3 ft) and at each end or joint, unless listed for other support intervals. In no case shall the distance between supports exceed 3 m (10 ft).

366.44 Expansion Fittings

Expansion fittings shall be installed where expected length change, due to expansion and contraction due to temperature change, is more than 6 mm (0.25 in.).

366.56 Splices and Taps

Splices and taps shall comply with 366.56(A) through (D).

(A) Within Gutters

Splices or taps shall be permitted within gutters where they are accessible by means of removable covers or doors. The conductors, including splices and taps, shall not fill the gutter to more than 75 percent of its area.

(B) Bare Conductors

Taps from bare conductors shall leave the gutter opposite their terminal connections, and conductors shall not be brought in contact with uninsulated current-carrying parts of different voltages.

(C) Suitably Identified

All taps shall be suitably identified at the gutter as to the circuit or equipment that they supply.

(D) Overcurrent Protection

Tap connections from conductors in auxiliary gutters shall be provided with overcurrent protection as required in 240.21.

366.58 Insulated Conductors

(A) Deflected Insulated Conductors

Where insulated conductors are deflected within an auxiliary gutter, either at the ends or where conduits, fittings, or other raceways or cables enter or leave the gutter, or where the direction of the gutter is deflected greater than 30 degrees, dimensions corresponding to one wire per terminal in Table 312.6(A) shall apply.

(B) Auxiliary Gutters Used as Pull Boxes

Where insulated conductors 4 AWG or larger are pulled through an auxiliary gutter, the distance between raceway and cable entries enclosing the same conductor shall not be less than that required in 314.28(A)(1) for straight pulls and 314.28(A)(2) for angle pulls.

366.60 Grounding

Metal auxiliary gutters shall be connected to an equipment grounding conductor(s), to an equipment bonding jumper, or to the grounded conductor where permitted or required by 250.92(B)(1) or 250.142.

Part III Construction Specifications

366.100 Construction

(A) Electrical and Mechanical Continuity

Gutters shall be constructed and installed so that adequate electrical and mechanical continuity of the complete system is secured.

(B) Substantial Construction

Gutters shall be of substantial construction and shall provide a complete enclosure for the contained conductors. All surfaces, both interior and exterior, shall be suitably protected from corrosion. Corner joints shall be made tight, and where the assembly is held together by rivets, bolts, or screws, such fasteners shall be spaced not more than 300 mm (12 in.) apart.

(C) Smooth Rounded Edges

Suitable bushings, shields, or fittings having smooth, rounded edges shall be provided where conductors pass between gutters, through partitions, around bends, between gutters and cabinets or junction boxes, and at other locations where necessary to prevent abrasion of the insulation of the conductors.

(D) Covers

Covers shall be securely fastened to the gutter.

(E) Clearance of Bare Live Parts

Bare conductors shall be securely and rigidly supported so that the minimum clearance between bare current-carrying metal parts of different voltages mounted on the same surface will not be less than 50 mm (2 in.), nor less than 25 mm (1 in.) for parts that are held free in the air. A clearance not less than 25 mm (1 in.) shall be secured between bare current-carrying metal parts and any metal surface. Adequate provisions shall be made for the expansion and contraction of busbars.

366.120 Marking

(A) Outdoors

Nonmetallic auxiliary gutters installed outdoors shall have the following markings:

Suitable for exposure to sunlight

Suitable for use in wet locations

Installed conductor insulation temperature rating

(B) Indoors

Nonmetallic auxiliary gutters installed indoors shall be marked with the installed conductor insulation temperature rating.

Article 368 Busways

Part I General Requirements

368.1 Scope

This article covers service-entrance, feeder, and branch-circuit busways and associated fittings.

368.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Busway. A raceway consisting of a metal enclosure containing factory-mounted, bare or insulated conductors, which are usually copper or aluminum bars, rods, or tubes.

Informational Note: For cablebus, refer to Article 370.

Part II Installation

368.10 Uses Permitted

Busways shall be permitted to be installed where they are located in accordance with 368.10(A) through (C).

Informational Note: See 300.21 for information concerning the spread of fire or products of combustion.

(A) Exposed

Busways shall be permitted to be located in the open where visible, except as permitted in 368.10(C).

(B) Behind Access Panels

Busways shall be permitted to be installed behind access panels, provided the busways are totally enclosed, of nonventilating-type construction, and installed so that the joints between sections and at fittings are accessible for maintenance purposes. Where installed behind access panels, means of access shall be provided, and either of the following conditions shall be met:

The space behind the access panels shall not be used for air-handling purposes.

Where the space behind the access panels is used for environmental air, other than ducts and plenums, there shall be no provisions for plug-in connections, and the conductors shall be insulated.

(C) Through Walls and Floors

Busways shall be permitted to be installed through walls or floors in accordance with (C)(1) and (C)(2).

(1) Walls

Unbroken lengths of busway shall be permitted to be extended through dry walls.

(2) Floors

Floor penetrations shall comply with (a) and (b):

(a) Busways shall be permitted to be extended vertically through dry floors if totally enclosed (unventilated) where passing through and for a minimum distance of 1.8 m (6 ft) above the floor to provide adequate protection from physical damage.

(b) In other than industrial establishments, where a vertical riser penetrates two or more dry floors, a minimum 100-mm (4-in.) high curb shall be installed around all floor openings for riser busways to prevent liquids from entering the opening. The curb shall be installed within 300 mm (12 in.) of the floor opening. Electrical equipment shall be located so that it will not be damaged by liquids that are retained by the curb.

368.12 Uses Not Permitted

(A) Physical Damage

Busways shall not be installed where subject to severe physical damage or corrosive vapors.

(B) Hoistways

Busways shall not be installed in hoistways.

Upcodes Diagrams

(C) Hazardous Locations

Busways shall not be installed in any hazardous (classified) location, unless specifically approved for such use.

Informational Note: See 501.10(B).

(D) Wet Locations

Busways shall not be installed outdoors or in wet or damp locations unless identified for such use.

(E) Working Platform

Lighting busway and trolley busway shall not be installed less than 2.5 m (8 ft) above the floor or working platform unless provided with an identified cover.

368.17 Overcurrent Protection

Overcurrent protection shall be provided in accordance with 368.17(A) through (D).

(A) Rating of Overcurrent Protection — Feeders

A busway shall be protected against overcurrent in accordance with the current rating of the busway.

Exception No. 1: The applicable provisions of 240.4 shall be permitted.

Exception No. 2: Where used as transformer secondary ties, 450.6(A)(3) shall be permitted.

(B) Reduction in Ampacity Size of Busway

Overcurrent protection shall be required where busways are reduced in ampacity.

Exception: For industrial establishments only, omission of overcurrent protection shall be permitted at points where busways are reduced in ampacity, provided that the length of the busway having the smaller ampacity does not exceed 15 m (50 ft) and has an ampacity at least equal to one-third the rating or setting of the overcurrent device next back on the line, and provided that such busway is free from contact with combustible material.

(C) Feeder or Branch Circuits

Where a busway is used as a feeder, devices or plug-in connections for tapping off feeder or branch circuits from the busway shall contain the overcurrent devices required for the protection of the feeder or branch circuits. The plug-in device shall consist of an externally operable circuit breaker or an externally operable fusible switch. Where such devices are mounted out of reach and contain disconnecting means, suitable means such as ropes, chains, or sticks shall be provided for operating the disconnecting means from the floor.

Exception No. 1: As permitted in 240.21.

Exception No. 2: For fixed or semifixed luminaires, where the branch-circuit overcurrent device is part of the luminaire cord plug on cord-connected luminaires.

Exception No. 3: Where luminaires without cords are plugged directly into the busway and the overcurrent device is mounted on the luminaire.

Exception No. 4: Where the branch-circuit overcurrent plug-in device is directly supplying a readily accessible disconnect, a method of floor operation shall not be required.

(D) Rating of Overcurrent Protection — Branch Circuits

A busway used as a branch circuit shall be protected against overcurrent in accordance with 210.20.

368.30 Support

Busways shall be securely supported at intervals not exceeding 1.5 m (5 ft) unless otherwise designed and marked.

368.56 Branches From Busways

Branches from busways shall be permitted to be made in accordance with 368.56(A), (B), and (C).

(A) General

Branches from busways shall be permitted to use any of the following wiring methods:

Type AC armored cable

Type MC metal-clad cable

Type MI mineral-insulated, metal-sheathed cable

Type IMC intermediate metal conduit

Type RMC rigid metal conduit

Type FMC flexible metal conduit

Type LFMC liquidtight flexible metal conduit

Type PVC rigid polyvinyl chloride conduit

Type RTRC reinforced thermosetting resin conduit

Type LFNC liquidtight flexible nonmetallic conduit

Type EMT electrical metallic tubing

Type ENT electrical nonmetallic tubing

Busways

Strut-type channel raceway

Surface metal raceway

Surface nonmetallic raceway

Where a separate equipment grounding conductor is used, connection of the equipment grounding conductor to the busway shall comply with 250.8 and 250.12.

(B) Cord and Cable Assemblies

Suitable cord and cable assemblies identified for extra-hard usage or hard usage and listed bus drop cable shall be permitted as branches from busways for the connection of portable equipment or the connection of stationary equipment to facilitate their interchange in accordance with 400.10 and 400.12 and the following conditions:

The cord or cable shall be attached to the building by an approved means.

The length of the cord or cable from a busway plug-in device to a suitable tension take-up support device shall not exceed 1.8 m (6 ft).

The cord and cable shall be installed as a vertical riser from the tension take-up support device to the equipment served.

Strain relief cable grips shall be provided for the cord or cable at the busway plug-in device and equipment terminations.

Exception to (B)(2): In industrial establishments only, where the conditions of maintenance and supervision ensure that only qualified persons service the installation, lengths exceeding 1.8 m (6 ft) shall be permitted between the busway plug-in device and the tension take-up support device where the cord or cable is supported at intervals not exceeding 2.5 m (8 ft).

(C) Branches From Trolley-Type Busways

Suitable cord and cable assemblies identified for extra-hard usage or hard usage and listed bus drop cable shall be permitted as branches from trolley-type busways for the connection of movable equipment in accordance with 400.10 and 400.12.

368.58 Dead Ends

A dead end of a busway shall be closed.

368.60 Grounding

Busway shall be connected to an equipment grounding conductor(s), to an equipment bonding jumper, or to the grounded conductor where permitted or required by 250.92(B)(1) or 250.142.

Part III Construction

368.120 Marking

Busways shall be marked with the voltage and current rating for which they are designed, and with the manufacturer's name or trademark in such a manner as to be visible after installation.

Part IV Requirements for Over 1000 Volts, Nominal

368.214 Adjacent and Supporting Structures

Metal-enclosed busways shall be installed so that temperature rise from induced circulating currents in adjacent ferrous metal parts will not be hazardous to personnel or constitute a fire hazard.

368.234 Barriers and Seals

(A) Vapor Seals

Busway runs that have sections located both inside and outside of buildings shall have a vapor seal at the building wall to prevent interchange of air between indoor and outdoor sections.

Exception: Vapor seals shall not be required in forced-cooled bus.

(B) Fire Barriers

Fire barriers shall be provided where fire walls, floors, or ceilings are penetrated.

Informational Note: See 300.21 for information concerning the spread of fire or products of combustion.

368.236 Drain Facilities

Drain plugs, filter drains, or similar methods shall be provided to remove condensed moisture from low points in busway run.

368.237 Ventilated Bus Enclosures

Ventilated busway enclosures shall be installed in accordance with Article 110, Part III, and 490.24.

368.238 Terminations and Connections

Where bus enclosures terminate at machines cooled by flammable gas, seal-off bushings, baffles, or other means shall be provided to prevent accumulation of flammable gas in the busway enclosures.

All conductor termination and connection hardware shall be accessible for installation, connection, and maintenance.

368.239 Switches

Switching devices or disconnecting links provided in the busway run shall have the same momentary rating as the busway. Disconnecting links shall be plainly marked to be removable only when bus is de-energized. Switching devices that are not load-break shall be interlocked to prevent operation under load, and disconnecting link enclosures shall be interlocked to prevent access to energized parts.

368.240 Wiring 1000 Volts or Less, Nominal

Secondary control devices and wiring that are provided as part of the metal-enclosed bus run shall be insulated by fire-retardant barriers from all primary circuit elements with the exception of short lengths of wire, such as at instrument transformer terminals.

368.244 Expansion Fittings

Flexible or expansion connections shall be provided in long, straight runs of bus to allow for temperature expansion or contraction, or where the busway run crosses building vibration insulation joints.

368.258 Neutral Conductor

Neutral bus, where required, shall be sized to carry all neutral load current, including harmonic currents, and shall have adequate momentary and short-circuit current rating consistent with system requirements.

368.260 Grounding

Metal-enclosed busway shall be grounded.

368.320 Marking

Each busway run shall be provided with a permanent nameplate on which the following information shall be provided:

Rated voltage.

Rated continuous current; if bus is forced-cooled, both the normal forced-cooled rating and the self-cooled (not forced-cooled) rating for the same temperature rise shall be given.

Rated frequency.

Rated impulse withstand voltage.

Rated 60-Hz withstand voltage (dry).

Rated momentary current.

Manufacturer's name or trademark.

Informational Note: See IEEE C37.23-2015, IEEE Standard for Metal-Enclosed Bus, for construction and testing requirements for metal-enclosed bus assemblies.

Article 370 Cablebus

Part I General

370.1 Scope

This article covers the use and installation requirements of cablebus and associated fittings.

370.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Cablebus. An assembly of units or sections with insulated conductors having associated fittings forming a structural system used to securely fasten or support conductors and conductor terminations in a completely enclosed, ventilated, protective metal housing. This assembly is designed to carry fault current and to withstand the magnetic forces of such current.

Informational Note: Cablebus is ordinarily assembled at the point of installation from the components furnished or specified by the manufacturer in accordance with instructions for the specific job.

Part II Installation

370.10 Uses Permitted

Approved cablebus shall be permitted:

At any voltage or current for which spaced conductors are rated and where installed only for exposed work, except as permitted in 370.18

For branch circuits, feeders, and services

To be installed outdoors or in corrosive, wet, or damp locations where identified for the use

370.12 Uses Not Permitted

Cablebus shall not be permitted to be installed in the following:

Hoistways

Hazardous (classified) locations, unless specifically permitted in Chapter 5

370.18 Cablebus Installation

(A) Transversely Routed

Cablebus shall be permitted to extend transversely through partitions or walls, other than fire walls, provided that the section within the wall is continuous, protected against physical damage, and unventilated.

(B) Through Dry Floors and Platforms

Except where firestops are required, cablebus shall be permitted to extend vertically through dry floors and platforms, provided that the cablebus is totally enclosed at the point where it passes through the floor or platform and for a distance of 1.8 m (6 ft) above the floor or platform.

(C) Through Floors and Platforms in Wet Locations

Except where firestops are required, cablebus shall be permitted to extend vertically through floors and platforms in wet locations where:

There are curbs or other suitable means to prevent water-flow through the floor or platform opening, and

Where the cablebus is totally enclosed at the point where it passes through the floor or platform and for a distance of 1.8 m (6 ft) above the floor or platform.

370.20 Conductor Size and Termination

(A) Conductors

The current-carrying conductors in cablebus shall:

Have an insulation rating of 75°C (167°F) or higher and be of an approved type suitable for the application.

Be sized in accordance with the design of the cablebus but in no case be smaller than 1/0.

(B) Termination

Approved terminating means shall be used for connections to cablebus conductors.

Informational Note No. 1: See 110.14(C) for conductor temperature limitations due to termination provisions for installations up to and including 2000 volts.

Informational Note No. 2: See 110.40 for conductor temperature limitations due to termination provisions for installations 2001 volts to 35,000 volts.

370.22 Number of Conductors

The number of conductors shall be that for which the cablebus is designed.

370.23 Overcurrent Protection

Cablebus shall be protected against overcurrent in accordance with the ampacity of the cablebus conductors in accordance with 240.4.

Exception: Overcurrent protection shall be permitted in accordance with 240.100 and 240.101.

370.30 Securing and Supporting

(A) Cablebus Supports

Cablebus shall be securely supported at intervals not exceeding 3.7 m (12 ft). Where spans longer than 3.7 m (12 ft) are required, the structure shall be specifically designed for the required span length.

(B) Conductor Supports

The insulated conductors shall be supported on blocks or other identified mounting means.

The individual conductors in a cablebus shall be supported at intervals not greater than 900 mm (3 ft) for horizontal runs and 450 mm (11/2 ft) for vertical runs. Vertical and horizontal spacing between supported conductors shall be not less than one conductor diameter at the points of support.

370.42 Fittings

A cablebus system shall include approved fittings for the following:

Changes in horizontal or vertical direction of the run

Dead ends

Terminations in or on connected apparatus or equipment or the enclosures for such equipment

Additional physical protection where required, such as guards where subject to severe physical damage

370.60 Grounding

A cablebus system shall be grounded and/or bonded as applicable:

Cablebus framework, where bonded, shall be permitted to be used as the equipment grounding conductor for branch circuits and feeders.

A cablebus installation shall be grounded and bonded in accordance with Article 250, excluding 250.86, Exception No. 2.

370.80 Ampacity of Conductors

The ampacity of conductors in cablebus shall be in accordance with 310.17 and 310.19 for installations up to and including 2000 volts, or with Table 311.60(C)(69) and Table 311.60(C)(70) for installations 2001 volts to 35,000 volts.

Part III Construction Specifications

370.120 Marking

Each section of cablebus shall be marked with the manufacturer's name or trade designation and the maximum diameter, number, voltage rating, and ampacity of the conductors to be installed. Markings shall be located so as to be visible after installation.

Article 372 Cellular Concrete Floor Raceways

Part I General

372.1 Scope

This article covers cellular concrete floor raceways, the hollow spaces in floors constructed of precast cellular concrete slabs, together with suitable metal fittings designed to provide access to the floor cells.

372.2 Definitions

The definitions in this section shall apply only within this article.

Cell. A single, enclosed tubular space in a floor made of precast cellular concrete slabs, the direction of the cell being parallel to the direction of the floor member.

Header. Transverse metal raceways for electrical conductors, providing access to predetermined cells of a precast cellular concrete floor, thereby permitting the installation of electrical conductors from a distribution center to the floor cells.

Part II Installations

372.12 Uses Not Permitted

Conductors shall not be installed in precast cellular concrete floor raceways as follows:

Where subject to corrosive vapor

In any hazardous (classified) location, except as permitted by other articles in this Code

In commercial garages, other than for supplying ceiling outlets or extensions to the area below the floor but not above

Informational Note: See 300.8 for installation of conductors with other systems.

372.18 Cellular Concrete Floor Raceways Installation

Installation of cellular concrete floor raceways shall comply with 372.18(A) through 372.18(E).

(A) Header

The header shall be installed in a straight line at right angles to the cells. The header shall be mechanically secured to the top of the precast cellular concrete floor. The end joints shall be closed by a metal closure fitting and sealed against the entrance of concrete. The header shall be electrically continuous throughout its entire length and shall be electrically bonded to the enclosure of the distribution center.

(B) Connection to Cabinets and Other Enclosures

Connections from headers to cabinets and other enclosures shall be made by means of listed metal raceways and listed fittings.

(C) Junction Boxes

Junction boxes shall be leveled to the floor grade and sealed against the free entrance of water or concrete. Junction boxes shall be of metal and shall be mechanically and electrically continuous with the header.

(D) Inserts

Inserts shall be leveled and sealed against the entrance of concrete. Inserts shall be of metal and shall be fitted with grounded-type receptacles. An equipment grounding conductor or bonding jumper shall connect the insert receptacles to a positive ground connection provided on the header. Where cutting through the cell wall for setting inserts or other purposes (such as providing access openings between header and cells), chips and other dirt shall not be allowed to remain in the raceway, and the tool used shall be designed so as to prevent the tool from entering the cell and damaging the conductors.

(E) Markers

A suitable number of markers shall be installed for the future location of cells.

372.20 Size of Conductors

No conductor larger than 1/0 AWG shall be installed, except by special permission.

372.22 Maximum Number of Conductors

The combined cross-sectional area of all conductors or cables shall not exceed 40 percent of the cross-sectional area of the cell or header.

372.23 Ampacity of Conductors

The ampacity adjustment factors as provided in 310.15(C) shall apply to conductors installed in cellular concrete floor raceways.

372.56 Splices and Taps

Splices and taps shall be made only in header access units or junction boxes. A continuous unbroken conductor connecting the individual outlets is not a splice or tap.

372.58 Discontinued Outlets

When an outlet is abandoned, discontinued, or removed, the sections of circuit conductors supplying the outlet shall be removed from the raceway. No splices or reinsulated conductors, such as would be the case of abandoned outlets on loop wiring, shall be allowed in raceways.

Article 374 Cellular Metal Floor Raceways

Part I General

374.1 Scope

This article covers the use and installation requirements for cellular metal floor raceways.

374.2 Definitions

The definitions in this section shall apply within this article and throughout the Code.

Cellular Metal Floor Raceway. The hollow spaces of cellular metal floors, together with suitable fittings, that may be approved as enclosed channel for electrical conductors.

Cell. A single enclosed tubular space in a cellular metal floor member, the axis of the cell being parallel to the axis of the metal floor member.

Header. A transverse raceway for electrical conductors, providing access to predetermined cells of a cellular metal floor, thereby permitting the installation of electrical conductors from a distribution center to the cells.

374.6 Listing Requirements

Cellular metal floor raceways shall be listed.

Part II Installation

374.12 Uses Not Permitted

Conductors shall not be installed in cellular metal floor raceways as follows:

Where subject to corrosive vapor

In any hazardous (classified) location, except as permitted by other articles in this Code

In commercial garages, other than for supplying ceiling outlets or extensions to the area below the floor but not above

Informational Note: See 300.8 for installation of conductors with other systems.

374.18 Cellular Metal Floor Raceways Installations

Installation of cellular metal floor raceways shall comply with 374.18(A) through 374.18(D).

(A) Connection to Cabinets and Extensions From Cells

Connections between raceways and distribution centers and wall outlets shall be made by means of liquidtight flexible metal conduit, flexible metal conduit where not installed in concrete, rigid metal conduit, intermediate metal conduit, electrical metallic tubing, or approved fittings. Where there are provisions for the termination of an equipment grounding conductor, rigid polyvinyl chloride conduit, reinforced thermosetting resin conduit, electrical nonmetallic tubing, or liquidtight flexible nonmetallic conduit shall be permitted. Where installed in concrete, liquidtight flexible metal conduit and liquidtight flexible nonmetallic conduit shall be listed and marked for direct burial.

(B) Junction Boxes

Junction boxes shall be leveled to the floor grade and sealed against the free entrance of water or concrete. Junction boxes used with these raceways shall be of metal and shall be electrically continuous with the raceway.

(C) Inserts

Inserts shall be leveled to the floor grade and sealed against the entrance of concrete. Inserts shall be of metal and shall be electrically continuous with the raceway. In cutting through the cell wall and setting inserts, chips and other dirt shall not be allowed to remain in the raceway, and tools shall be used that are designed to prevent the tool from entering the cell and damaging the conductors.

(D) Markers

A suitable number of markers shall be installed for locating cells in the future.

374.20 Size of Conductors

No conductor larger than 1/0 AWG shall be installed, except by special permission.

374.22 Maximum Number of Conductors in Raceway

The combined cross-sectional area of all conductors or cables shall not exceed 40 percent of the interior cross-sectional area of the cell or header.

374.23 Ampacity of Conductors

The ampacity adjustment factors in 310.15(C) shall apply to conductors installed in cellular metal floor raceways.

374.56 Splices and Taps

Splices and taps shall be made only in header access units or junction boxes.

For the purposes of this section, so-called loop wiring (continuous unbroken conductor connecting the individual outlets) shall not be considered to be a splice or tap.

374.58 Discontinued Outlets

When an outlet is abandoned, discontinued, or removed, the sections of circuit conductors supplying the outlet shall be removed from the raceway. No splices or reinsulated conductors, such as would be the case with abandoned outlets on loop wiring, shall be allowed in raceways.

Part III Construction Specifications

374.100 General

Cellular metal floor raceways shall be constructed so that adequate electrical and mechanical continuity of the complete system will be secured. They shall provide a complete enclosure for the conductors. The interior surfaces shall be free from burrs and sharp edges, and surfaces over which conductors are drawn shall be smooth. Suitable bushings or fittings having smooth rounded edges shall be provided where conductors pass.

Article 376 Metal Wireways

Part I General

376.1 Scope

This article covers the use, installation, and construction specifications for metal wireways and associated fittings.

376.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Metal Wireways. Sheet metal troughs with hinged or removable covers for housing and protecting electrical wires and cable and in which conductors are laid in place after the raceway has been installed as a complete system.

Part II Installation

376.10 Uses Permitted

The use of metal wireways shall be permitted as follows:

For exposed work.

In any hazardous (classified) location, as permitted by other articles in this Code.

In wet locations where wireways are listed for the purpose.

In concealed spaces as an extension that passes transversely through walls, if the length passing through the wall is unbroken. Access to the conductors shall be maintained on both sides of the wall.

376.12 Uses Not Permitted

Metal wireways shall not be used in the following:

Where subject to severe physical damage

Where subject to severe corrosive environments

376.20 Conductors Connected in Parallel

Where single conductor cables comprising each phase, neutral, or grounded conductor of an alternating-current circuit are connected in parallel as permitted in 310.10(G), the conductors shall be installed in groups consisting of not more than one conductor per phase, neutral, or grounded conductor.

Informational Note: The purpose of having all parallel conductor sets within the same group is to prevent current imbalance in the paralleled conductors due to inductive reactance.

376.21 Size of Conductors

No conductor larger than that for which the wireway is designed shall be installed in any wireway.

376.22 Number of Conductors and Ampacity

The number of conductors or cables and their ampacity shall comply with 376.22(A) and (B).

(A) Cross-Sectional Areas of Wireway

The sum of the crosssectional areas of all contained conductors and cables at any cross section of a wireway shall not exceed 20 percent of the interior cross-sectional area of the wireway.

(B) Adjustment Factors

The adjustment factors in 310.15(C)(1) shall be applied only where the number of current-carrying conductors, including neutral conductors classified as current-carrying under 310.15(E), exceeds 30 at any cross section of the wireway. Conductors for signaling circuits or controller conductors between a motor and its starter and used only for starting duty shall not be considered as current-carrying conductors.

376.23 Insulated Conductors

Insulated conductors installed in a metal wireway shall comply with 376.23(A) and (B).

(A) Deflected Insulated Conductors

Where insulated conductors are deflected within a metal wireway, either at the ends or where conduits, fittings, or other raceways or cables enter or leave the metal wireway, or where the direction of the metal wireway is deflected greater than 30 degrees, dimensions corresponding to one wire per terminal in Table 312.6(A) shall apply.

(B) Metal Wireways Used as Pull Boxes

Where insulated conductors 4 AWG or larger are pulled through a wireway, the distance between raceway and cable entries enclosing the same conductor shall not be less than that required by 314.28(A)(1) for straight pulls and 314.28(A)(2) for angle pulls. When transposing cable size into raceway size, the minimum metric designator (trade size) raceway required for the number and size of conductors in the cable shall be used.

376.30 Securing and Supporting

Metal wireways shall be supported in accordance with 376.30(A) and (B).

(A) Horizontal Support

Wireways shall be supported where run horizontally at each end and at intervals not to exceed 1.5 m (5 ft) or for individual lengths longer than 1.5 m (5 ft) at each end or joint, unless listed for other support intervals. The distance between supports shall not exceed 3 m (10 ft).

(B) Vertical Support

Vertical runs of wireways shall be securely supported at intervals not exceeding 4.5 m (15 ft) and shall not have more than one joint between supports. Adjoining wireway sections shall be securely fastened together to provide a rigid joint.

376.56 Splices, Taps, and Power Distribution Blocks

(A) Splices and Taps

Splices and taps shall be permitted within a wireway, provided they are accessible. The conductors, including splices and taps, shall not fill the wireway to more than 75 percent of its area at that point.

(B) Power Distribution Blocks

(1) Installation

Power distribution blocks installed in metal wireways shall be listed. Power distribution blocks installed on the line side of the service equipment shall be marked "suitable for use on the line side of service equipment" or equivalent.

(2) Size of Enclosure

In addition to the wiring space requirement in 376.56(A), the power distribution block shall be installed in a wireway with dimensions not smaller than specified in the installation instructions of the power distribution block.

(3) Wire Bending Space

Wire bending space at the terminals of power distribution blocks shall comply with 312.6(B).

(4) Live Parts

Power distribution blocks shall not have uninsulated live parts exposed within a wireway, whether or not the wireway cover is installed.

(5) Conductors

Conductors shall be arranged so the power distribution block terminals are unobstructed following installation.

376.58 Dead Ends

Dead ends of metal wireways shall be closed.

376.70 Extensions From Metal Wireways

Extensions from wireways shall be made with cord pendants installed in accordance with 400.14 or with any wiring method in Chapter 3 that includes a means for equipment grounding. Where a separate equipment grounding conductor is employed, connection of the equipment grounding conductors in the wiring method to the wireway shall comply with 250.8 and 250.12.

Part III Construction Specifications

376.100 Construction

(A) Electrical and Mechanical Continuity

Wireways shall be constructed and installed so that electrical and mechanical continuity of the complete system are assured.

(B) Substantial Construction

Wireways shall be of substantial construction and shall provide a complete enclosure for the contained conductors. All surfaces, both interior and exterior, shall be suitably protected from corrosion. Corner joints shall be made tight, and where the assembly is held together by rivets, bolts, or screws, such fasteners shall be spaced not more than 300 mm (12 in.) apart.

(C) Smooth Rounded Edges

Suitable bushings, shields, or fittings having smooth, rounded edges shall be provided where conductors pass between wireways, through partitions, around bends, between wireways and cabinets or junction boxes, and at other locations where necessary to prevent abrasion of the insulation of the conductors.

(D) Covers

Covers shall be securely fastened to the wireway.

376.120 Marking

Metal wireways shall be so marked that their manufacturer's name or trademark will be visible after installation.

Article 378 Nonmetallic Wireways

Part I General

378.1 Scope

This article covers the use, installation, and construction specifications for nonmetallic wireways and associated fittings.

378.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Nonmetallic Wireways. Flame-retardant, nonmetallic troughs with removable covers for housing and protecting electrical wires and cables in which conductors are laid in place after the raceway has been installed as a complete system.

378.6 Listing Requirements

Nonmetallic wireways and associated fittings shall be listed.

Part II Installation

378.10 Uses Permitted

The use of nonmetallic wireways shall be permitted in the following:

Only for exposed work, except as permitted in 378.10(4).

Where subject to corrosive environments where identified for the use.

In wet locations where listed for the purpose.

Informational Note: Extreme cold may cause nonmetallic wireways to become brittle and therefore more susceptible to damage from physical contact.

As extensions to pass transversely through walls if the length passing through the wall is unbroken. Access to the conductors shall be maintained on both sides of the wall.

378.12 Uses Not Permitted

Nonmetallic wireways shall not be used in the following:

Where subject to physical damage

In any hazardous (classified) location, except as permitted by other articles in this Code

Where exposed to sunlight unless listed and marked as suitable for the purpose

Where subject to ambient temperatures other than those for which nonmetallic wireway is listed

For conductors whose insulation temperature limitations would exceed those for which the nonmetallic wireway is listed

378.20 Conductors Connected in Parallel

Where single conductor cables comprising each phase, neutral, or grounded conductor of an alternating-current circuit are connected in parallel as permitted in 310.10(G), the conductors shall be installed in groups consisting of not more than one conductor per phase, neutral, or grounded conductor to prevent current imbalance in the paralleled conductors due to inductive reactance.

378.21 Size of Conductors

No conductor larger than that for which the nonmetallic wire way is designed shall be installed in any nonmetallic wireway.

378.22 Number of Conductors

The sum of cross-sectional areas of all contained conductors or cables at any cross section of the nonmetallic wireway shall not exceed 20 percent of the interior cross-sectional area of the nonmetallic wireway. Conductors for signaling circuits or controller conductors between a motor and its starter and used only for starting duty shall not be considered as current-carrying conductors.

The adjustment factors specified in 310.15(C)(1) shall be applicable to the current-carrying conductors up to and including the 20 percent fill specified in the first paragraph of this section.

378.23 Insulated Conductors

Insulated conductors installed in a nonmetallic wireway shall comply with 378.23(A) and (B).

(A) Deflected Insulated Conductors

Where insulated conductors are deflected within a nonmetallic wireway, either at the ends or where conduits, fittings, or other raceways or cables enter or leave the nonmetallic wireway, or where the direction of the nonmetallic wireway is deflected greater than 30 degrees, dimensions corresponding to one wire per terminal in Table 312.6(A) shall apply.

(B) Nonmetallic Wireways Used as Pull Boxes

Where insulated conductors 4 AWG or larger are pulled through a wireway, the distance between raceway and cable entries enclosing the same conductor shall not be less than that required in 314.28(A)(1) for straight pulls and in 314.28(A)(2) for angle pulls. When transposing cable size into raceway size, the minimum metric designator (trade size) raceway required for the number and size of conductors in the cable shall be used.

378.30 Securing and Supporting

Nonmetallic wireway shall be supported in accordance with 378.30(A) and (B).

(A) Horizontal Support

Nonmetallic wireways shall be supported where run horizontally at intervals not to exceed 900 mm (3 ft), and at each end or joint, unless listed for other support intervals. In no case shall the distance between supports exceed 3 m (10 ft).

(B) Vertical Support

Vertical runs of nonmetallic wireway shall be securely supported at intervals not exceeding 1.2 m (4 ft), unless listed for other support intervals, and shall not have more than one joint between supports. Adjoining nonmetallic wireway sections shall be securely fastened together to provide a rigid joint.

378.44 Expansion Fittings

Expansion fittings for nonmetallic wireway shall be provided to compensate for thermal expansion and contraction where the length change is expected to be 6 mm (0.25 in.) or greater in a straight run.

Informational Note: See Table 352.44 for expansion characteristics of PVC conduit. The expansion characteristics of PVC nonmetallic wireway are identical.

378.56 Splices and Taps

Splices and taps shall be permitted within a nonmetallic wireway, provided they are accessible. The conductors, including splices and taps, shall not fill the nonmetallic wireway to more than 75 percent of its area at that point.

378.58 Dead Ends

Dead ends of nonmetallic wireway shall be closed using listed fittings.

378.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the nonmetallic wireway. A separate equipment grounding conductor shall not be required where the grounded conductor is used to ground equipment as permitted in 250.142.

378.70 Extensions From Nonmetallic Wireways

Extensions from nonmetallic wireway shall be made with cord pendants or any wiring method of Chapter 3. A separate equipment grounding conductor shall be installed in, or an equipment grounding connection shall be made to, any of the wiring methods used for the extension.

Part III Construction Specifications

378.120 Marking

Nonmetallic wireways shall be marked so that the manufacturer's name or trademark and interior cross-sectional area in square inches shall be visible after installation. Marking for limited smoke shall be permitted on the nonmetallic wireways that have limited smoke-producing characteristics.

Article 380 Multioutlet Assembly

Part I General

380.1 Scope

This article covers the use and installation requirements for multioutlet assemblies.

Informational Note: See the definition of multioutlet assembly in Article 100.

Part II Installation

380.10 Uses Permitted

The use of a multioutlet assembly shall be permitted in dry locations.

380.12 Uses Not Permitted

A multioutlet assembly shall not be installed as follows:

Where concealed, except that it shall be permissible to surround the back and sides of a metal multioutlet assembly by the building finish or recess a nonmetallic multioutlet assembly in a baseboard

Where subject to severe physical damage

Where the voltage is 300 volts or more between conductors unless the assembly is of metal having a thickness of not less than 1.02 mm (0.040 in.)

Where subject to corrosive vapors

In hoistways

In any hazardous (classified) location, except as permitted by other articles in this Code

Where cord and plug connected

380.23 Insulated Conductors

For field-assembled multioutlet assemblies, insulated conductors shall comply with 380.23(A) and (B), as applicable.

(A) Deflected Insulated Conductors

Where insulated conductors are deflected within a multioutlet assembly, either at the ends or where conduits, fittings, or other raceways or cables enter or leave the multioutlet assembly, or where the direction of the multioutlet assembly is deflected greater than 30 degrees, dimensions corresponding to one wire per terminal in Table 312.6(A) shall apply.

(B) Multioutlet Assemblies Used as Pull Boxes

Where insulated conductors 4 AWG or larger are pulled through a multioutlet assembly, the distance between raceway and cable entries enclosing the same conductor shall not be less than that required by 314.28(A)(1) for straight pulls and 314.28(A)(2) for angle pulls. When transposing cable size into raceway size, the minimum metric designator (trade size) raceway required for the number and size of conductors in the cable shall be used.

380.76 Metal Multioutlet Assembly Through Dry Partitions

It shall be permissible to extend a metal multioutlet assembly through (not run within) dry partitions if arrangements are made for removing the cap or cover on all exposed portions and no outlet is located within the partitions.

Article 382 Nonmetallic Extensions

Part I General

382.1 Scope

This article covers the use, installation, and construction specifications for nonmetallic extensions.

382.2 Definitions

The definitions in this section shall apply within this article and throughout the Code.

Concealable Nonmetallic Extension. A listed assembly of two, three, or four insulated circuit conductors within a nonmetallic jacket, an extruded thermoplastic covering, or a sealed nonmetallic covering. The classification includes surface extensions intended for mounting directly on the surface of walls or ceilings and concealed with paint, texture, joint compound, plaster, wallpaper, tile, wall paneling, or other similar materials.

Nonmetallic Extension. An assembly of two insulated conductors within a nonmetallic jacket or an extruded thermoplastic covering. The classification includes surface extensions intended for mounting directly on the surface of walls or ceilings.

382.6 Listing Requirements

Concealable nonmetallic extensions and associated fittings and devices shall be listed. The starting/source tap device for the extension shall contain and provide the following protection for all load-side extensions and devices:

Supplementary overcurrent protection

Level of protection equivalent to a Class A GFCI

Level of protection equivalent to a portable GFCI

Line and load-side miswire protection

Provide protection from the effects of arc faults

Part II Installation

382.10 Uses Permitted

Nonmetallic extensions shall be permitted only in accordance with 382.10(A), (B), and (C).

(A) From an Existing Outlet

The extension shall be from an existing outlet on a 15- or 20-ampere branch circuit. Where a concealable nonmetallic extension originates from a non—grounding-type receptacle, the installation shall comply with 250.130(C), 406.4(D)(2)(b), or 406.4(D)(2)(c).

(B) Exposed and in a Dry Location

The extension shall be run exposed, or concealed as permitted in 382.15, and in a dry location.

(C) Residential or Offices

For nonmetallic surface extensions mounted directly on the surface of walls or ceilings, the building shall be occupied for residential or office purposes and shall not exceed three floors abovegrade. Where identified for the use, concealable nonmetallic extensions shall be permitted more than three floors abovegrade.

Informational Note No. 1: See 310.14(A)(3) for temperature limitation of conductors.

Informational Note No. 2: See 362.10 for definition of First Floor.

382.12 Uses Not Permitted

Nonmetallic extensions shall not be used as follows:

In unfinished basements, attics, or roof spaces

Where the voltage between conductors exceeds 150 volts for nonmetallic surface extensions and 300 volts for aerial cable

Where subject to corrosive vapors

Where run through a floor or partition, or outside the room in which it originates

382.15 Exposed

(A) Nonmetallic Extensions

One or more extensions shall be permitted to be run in any direction from an existing outlet, but not on the floor or within 50 mm (2 in.) from the floor.

(B) Concealable Nonmetallic Extensions

Where identified for the use, nonmetallic extensions shall be permitted to be concealed with paint, texture, concealing compound, plaster, wallpaper, tile, wall paneling, or other similar materials and installed in accordance with 382.15(A).

382.26 Bends

(A) Nonmetallic Extensions

A bend that reduces the normal spacing between the conductors shall be covered with a cap to protect the assembly from physical damage.

(B) Concealable Nonmetallic Extensions

Concealable extensions shall be permitted to be folded back over themselves and flattened as required for installation.

382.30 Securing and Supporting

(A) Nonmetallic Extensions

Nonmetallic surface extensions shall be secured in place by approved means at intervals not exceeding 200 mm (8 in.), with an allowance for 300 mm (12 in.) to the first fastening where the connection to the supplying outlet is by means of an attachment plug. There shall be at least one fastening between each two adjacent outlets supplied. An extension shall be attached to only woodwork or plaster finish and shall not be in contact with any metal work or other conductive material other than with metal plates on receptacles.

(B) Concealable Nonmetallic Extensions

All surface-mounted concealable nonmetallic extension components shall be firmly anchored to the wall or ceiling using an adhesive or mechanical anchoring system identified for this use.

382.40 Boxes and Fittings

Each run shall terminate in a fitting, connector, or box that covers the end of the assembly. All fittings, connectors, and devices shall be of a type identified for the use.

382.42 Devices

(A) Receptacles

All receptacles, receptacle housings, and self-contained devices used with concealable nonmetallic extensions shall be identified for this use.

(B) Receptacles and Housings

Receptacle housings and self-contained devices designed either for surface or for recessed mounting shall be permitted for use with concealable nonmetallic extensions. Receptacle housings and self-contained devices shall incorporate means for facilitating entry and termination of concealable nonmetallic extensions and for electrically connecting the housing or device. Receptacle and self-contained devices shall comply with 406.4. Power and communications outlets installed together in common housing shall be permitted in accordance with 805.133(A)(1)(c), Exception No. 2.

382.56 Splices and Taps

Extensions shall consist of a continuous unbroken length of the assembly, without splices, and without exposed conductors between fittings, connectors, or devices. Taps shall be permitted where approved fittings completely covering the tap connections are used. Aerial cable and its tap connectors shall be provided with an approved means for polarization. Receptacle-type tap connectors shall be of the locking type.

Part III Construction Specifications (Concealable Nonmetallic Extensions Only)

382.100 Construction

Concealable nonmetallic extensions shall be of a multilayer flat conductor design consisting of a center ungrounded conductor enclosed by a sectioned grounded conductor and an overall sectioned equipment grounding conductor.

382.104 Flat Conductors

Concealable nonmetallic extensions shall be constructed, using flat copper conductors equivalent to 14 AWG or 12 AWG conductor sizes, and constructed per 382.104(A), (B), and (C).

(A) Ungrounded Conductor (Center Layer)

The ungrounded conductor shall consist of one or more ungrounded flat conductor(s) enclosed in accordance with 382.104(B) and (C) and identified in accordance with 310.6(C).

(B) Grounded Conductor (Inner Sectioned Layers)

The grounded conductor shall consist of two sectioned inner flat conductors that enclose the center ungrounded conductor(s). The sectioned grounded conductor shall be enclosed by the sectioned equipment grounding conductor and identified in accordance with 200.6.

(C) Equipment Grounding Conductor (Outer Sectioned Layers)

The equipment grounding conductor shall consist of two overall sectioned conductors that enclose the grounded conductor and ungrounded conductor(s) and shall comply with 250.4(A)(5). The equipment grounding conductor layers shall be identified by any one of the following methods:

As permitted in 250.119

A clear covering

One or more continuous green stripes or hash marks

The term "Equipment Grounding Conductor" printed at regular intervals throughout the cable

382.112 Insulation

The ungrounded and grounded flat conductor layers shall be individually insulated and comply with 310.14(A)(3). The equipment grounding conductor shall be covered or insulated.

382.120 Marking

(A) Cable

Concealable nonmetallic extensions shall be clearly and durably marked on both sides at intervals of not more than 610 mm (24 in.) with the information required by 310.8(A) and with the following additional information:

Material of conductors

Maximum temperature rating

Ampacity

(B) Conductor Identification

Conductors shall be clearly and durably identified on both sides throughout their length as specified in 382.104.

Article 384 Strut-Type Channel Raceway

Part I General

384.1 Scope

This article covers the use, installation, and construction specifications of strut-type channel raceway.

384.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Strut-Type Channel Raceway. A metal raceway that is intended to be mounted to the surface of or suspended from a structure, with associated accessories for the installation of electrical conductors and cables.

384.6 Listing Requirements

Strut-type channel raceways and accessories shall be listed and identified for such use.

Part II Installation

384.10 Uses Permitted

The use of strut-type channel raceways shall be permitted in the following:

Where exposed.

In dry locations.

In locations subject to corrosive vapors where protected by finishes approved for the condition.

As power poles.

In hazardous (classified) locations as permitted in Chapter 5.

As extensions of unbroken lengths through walls, partitions, and floors where closure strips are removable from either side and the portion within the wall, partition, or floor remains covered.

Ferrous channel raceways and fittings protected from corrosion solely by enamel shall be permitted only indoors.

384.12 Uses Not Permitted

Strut-type channel raceways shall not be used as follows:

Where concealed.

Ferrous channel raceways and fittings protected from corrosion solely by enamel shall not be permitted where subject to severe corrosive influences.

384.21 Size of Conductors

No conductor larger than that for which the raceway is listed shall be installed in strut-type channel raceways.

384.22 Number of Conductors

The number of conductors or cables permitted in strut-type channel raceways shall not exceed the percentage fill using Table 384.22 and applicable cross-sectional area of specific types and sizes of wire given in the tables in Chapter 9.

The adjustment factors of 310.15(C)(1) shall not apply to conductors installed in strut-type channel raceways where all of the following conditions are met:

The cross-sectional area of the raceway exceeds 2500 mm2 (4 in.2).

The current-carrying conductors do not exceed 30 in number.

The sum of the cross-sectional areas of all contained conductors does not exceed 20 percent of the interior cross-sectional area of the strut-type channel raceways.

Table 384.22 Channel Size and Inside Cross-Sectional Area

Area 40% Area\* 25% Area†

Size Channel in.2 mm2 in.2 mm2 in.2 mm2

15/8 × 15/16 0.887 572 0.355 229 0.222 143

15/8 × 1 1.151 743 0.460 297 0.288 186

15/8 × 13/8 1.677 1076 0.671 433 0.419 270

15/8 × 15/8 2.028 1308 0.811 523 0.507 327

15/8 × 27/16 3.169 2045 1.267 817 0.792 511

15/8 × 31/4 4.308 2780 1.723 1112 1.077 695

11/2 × 3/4 0.849 548 0.340 219 0.212 137

11/2 × 11/2 1.828 1179 0.731 472 0.457 295

11/2 × 17/8 2.301 1485 0.920 594 0.575 371

11/2 × 3 3.854 2487 1.542 995 0.964 622

\*Raceways with external joiners shall use a 40 percent wire fill calculation to determine the number of conductors permitted.

†Raceways with internal joiners shall use a 25 percent wire fill calculation to determine the number of conductors permitted.

384.30 Securing and Supporting

(A) Surface Mount

A surface mount strut-type channel raceway shall be secured to the mounting surface with retention straps external to the channel at intervals not exceeding 3 m (10 ft) and within 900 mm (3 ft) of each outlet box, cabinet, junction box, or other channel raceway termination.

(B) Suspension Mount

Strut-type channel raceways shall be permitted to be suspension mounted in air with identified methods at intervals not to exceed 3 m (10 ft) and within 900 mm (3 ft) of channel raceway terminations and ends.

384.56 Splices and Taps

Splices and taps shall be permitted in raceways that are accessible after installation by having a removable cover. The conductors, including splices and taps, shall not fill the raceway to more than 75 percent of its area at that point. All splices and taps shall be made by approved methods.

384.60 Grounding

Strut-type channel raceway enclosures providing a transition to or from other wiring methods shall have a means for connecting an equipment grounding conductor. Strut-type channel raceways shall be permitted as an equipment grounding conductor in accordance with 250.118(13). Where a snap-fit metal cover for strut-type channel raceways is used to achieve electrical continuity in accordance with the listing, this cover shall not be permitted as the means for providing electrical continuity for a receptacle mounted in the cover.

Part III Construction Specifications

384.100 Construction

Strut-type channel raceways and their accessories shall be of a construction that distinguishes them from other raceways. Raceways and their elbows, couplings, and other fittings shall be designed such that the sections can be electrically and mechanically coupled together and installed without subjecting the wires to abrasion. They shall comply with 384.100(A), (B), and (C).

(A) Material

Raceways and accessories shall be formed of steel, stainless steel, or aluminum.

(B) Corrosion Protection

Steel raceways and accessories shall be protected against corrosion by galvanizing or by an organic coating.

Informational Note: Enamel and PVC coatings are examples of organic coatings that provide corrosion protection.

(C) Cover

Covers of strut-type channel raceways shall be either metal or nonmetallic.

384.120 Marking

Each length of strut-type channel raceway shall be clearly and durably identified as required in the first sentence of 110.21(A).

Article 386 Surface Metal Raceways

Part I General

386.1 Scope

This article covers the use, installation, and construction specifications for surface metal raceways and associated fittings.

386.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Surface Metal Raceway. A metal raceway that is intended to be mounted to the surface of a structure, with associated couplings, connectors, boxes, and fittings for the installation of electrical conductors.

386.6 Listing Requirements

Surface metal raceway and associated fittings shall be listed.

Part II Installation

386.10 Uses Permitted

The use of surface metal raceways shall be permitted in the following:

In dry locations.

In Class I, Division 2 hazardous (classified) locations as permitted in 501.10(B)(3).

Under raised floors, as permitted in 645.5(E)(2).

Extension through walls and floors. Surface metal raceway shall be permitted to pass transversely through dry walls, dry partitions, and dry floors if the length passing through is unbroken. Access to the conductors shall be maintained on both sides of the wall, partition, or floor.

386.12 Uses Not Permitted

Surface metal raceways shall not be used in the following:

Where subject to severe physical damage, unless otherwise approved

Where the voltage is 300 volts or more between conductors, unless the metal has a thickness of not less than 1.02 mm (0.040 in.) nominal

Where subject to corrosive vapors

In hoistways

Where concealed, except as permitted in 386.10

386.21 Size of Conductors

No conductor larger than that for which the raceway is designed shall be installed in surface metal raceway.

386.22 Number of Conductors or Cables

The number of conductors or cables installed in surface metal raceway shall not be greater than the number for which the raceway is designed. Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles.

The adjustment factors of 310.15(C)(1) shall not apply to conductors installed in surface metal raceways where all of the following conditions are met:

The cross-sectional area of the raceway exceeds 2500 mm2 (4 in.2).

The current-carrying conductors do not exceed 30 in number.

The sum of the cross-sectional areas of all contained conductors does not exceed 20 percent of the interior cross-sectional area of the surface metal raceway.

386.30 Securing and Supporting

Surface metal raceways and associated fittings shall be supported in accordance with the manufacturer's installation instructions.

386.56 Splices and Taps

Splices and taps shall be permitted in surface metal raceways having a removable cover that is accessible after installation. The conductors, including splices and taps, shall not fill the raceway to more than 75 percent of its area at that point. Splices and taps in surface metal raceways without removable covers shall be made only in boxes. All splices and taps shall be made by approved methods.

Taps of Type FC cable installed in surface metal raceway shall be made in accordance with 322.56(B).

386.60 Grounding

Surface metal raceway enclosures providing a transition from other wiring methods shall have a means for connecting an equipment grounding conductor.

386.70 Combination Raceways

When combination surface metal raceways are used for both signaling and for lighting and power circuits, the different systems shall be run in separate compartments identified by stamping, imprinting, or color coding of the interior finish.

Part III Construction Specifications

386.100 Construction

Surface metal raceways shall be of such construction as will distinguish them from other raceways. Surface metal raceways and their elbows, couplings, and similar fittings shall be designed so that the sections can be electrically and mechanically coupled together and installed without subjecting the wires to abrasion.

Where covers and accessories of nonmetallic materials are used on surface metal raceways, they shall be identified for such use.

386.120 Marking

Each length of surface metal raceway shall be clearly and durably identified as required in the first sentence of 110.21(A).

Article 388 Surface Nonmetallic Raceways

Part I General

388.1 Scope

This article covers the use, installation, and construction specifications for surface nonmetallic raceways and associated fittings.

388.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Surface Nonmetallic Raceway. A nonmetallic raceway that is intended to be mounted to the surface of a structure, with associated couplings, connectors, boxes, and fittings for the installation of electrical conductors.

388.6 Listing Requirements

Surface nonmetallic raceway and associated fittings shall be listed.

Part II Installation

388.10 Uses Permitted

Surface nonmetallic raceways shall be permitted as follows:

The use of surface nonmetallic raceways shall be permitted in dry locations.

Extension through walls and floors shall be permitted. Surface nonmetallic raceway shall be permitted to pass transversely through dry walls, dry partitions, and dry floors if the length passing through is unbroken. Access to the conductors shall be maintained on both sides of the wall, partition, or floor.

388.12 Uses Not Permitted

Surface nonmetallic raceways shall not be used in the following:

Where concealed, except as permitted in 388.10(2)

Where subject to severe physical damage

Where the voltage is 300 volts or more between conductors, unless listed for higher voltage

In hoistways

In any hazardous (classified) location, except as permitted by other articles in this Code

Where subject to ambient temperatures exceeding those for which the nonmetallic raceway is listed

For conductors whose insulation temperature limitations would exceed those for which the nonmetallic raceway is listed

388.21 Size of Conductors

No conductor larger than that for which the raceway is designed shall be installed in surface nonmetallic raceway.

388.22 Number of Conductors or Cables

The number of conductors or cables installed in surface nonmetallic raceway shall not be greater than the number for which the raceway is designed. Cables shall be permitted to be installed where such use is not prohibited by the respective cable articles.

388.30 Securing and Supporting

Surface nonmetallic raceways and associated fittings shall be supported in accordance with the manufacturer's installation instructions.

388.56 Splices and Taps

Splices and taps shall be permitted in surface nonmetallic raceways having a cover capable of being opened in place that is accessible after installation. The conductors, including splices and taps, shall not fill the raceway to more than 75 percent of its area at that point. Splices and taps in surface nonmetallic raceways without covers capable of being opened in place shall be made only in boxes. All splices and taps shall be made by approved methods.

388.60 Grounding

Where equipment grounding is required, a separate equipment grounding conductor shall be installed in the raceway.

388.70 Combination Raceways

When combination surface nonmetallic raceways are used both for signaling and for lighting and power circuits, the different systems shall be run in separate compartments identified by stamping, imprinting, or color coding of the interior finish.

Part III Construction Specifications

388.100 Construction

Surface nonmetallic raceways shall be of such construction as will distinguish them from other raceways. Surface nonmetallic raceways and their elbows, couplings, and similar fittings shall be designed so that the sections can be mechanically coupled together and installed without subjecting the wires to abrasion.

Surface nonmetallic raceways and fittings are made of suitable nonmetallic material that is resistant to moisture and chemical atmospheres. It shall also be flame retardant, resistant to impact and crushing, resistant to distortion from heat under conditions likely to be encountered in service, and resistant to low-temperature effects.

388.120 Marking

Surface nonmetallic raceways that have limited smoke-producing characteristics shall be permitted to be so identified. Each length of surface nonmetallic raceway shall be clearly and durably identified as required in the first sentence of 110.21(A).

Article 390 Underfloor Raceways

Part I General

390.1 Scope

This article covers the use and installation requirements for underfloor raceways.

390.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Underfloor Raceway. A raceway and associated components designed and intended for installation beneath or flush with the surface of a floor for the installation of cables and electrical conductors.

Part II Installation

390.10 Uses Permitted

The installation of underfloor raceways shall be permitted beneath the surface of concrete or other flooring material or in office occupancies where laid flush with the concrete floor and covered with linoleum or equivalent floor covering.

390.12 Uses Not Permitted

Underfloor raceways shall not be installed (1) where subject to corrosive vapors or (2) in any hazardous (classified) locations, except as permitted by 504.20 and in Class I, Division 2 locations as permitted in 501.10(B)(3). Unless made of a material approved for the condition or unless corrosion protection approved for the condition is provided, metal underfloor raceways, junction boxes, and fittings shall not be installed in concrete or in areas subject to severe corrosive influences.

390.15 Covering

Raceway coverings shall comply with 390.15(A) through (D).

(A) Raceways Not Over 100 mm (4 In.) Wide

Half-round and flat-top raceways not over 100 mm (4 in.) in width shall have not less than 20 mm (3/4 in.) of concrete or wood above the raceway.

Exception: As permitted in 390.15(C) and (D) for flat-top raceways.

(B) Raceways Over 100 mm (4 In.) Wide but Not Over 200 mm (8 In.) Wide

Flat-top raceways over 100 mm (4 in.) but not over 200 mm (8 in.) wide with a minimum of 25 mm (1 in.) spacing between raceways shall be covered with concrete to a depth of not less than 25 mm (1 in.). Raceways spaced less than 25 mm (1 in.) apart shall be covered with concrete to a depth of 38 mm (11/2 in.).

(C) Trench-Type Raceways Flush With Concrete

Trench-type flush raceways with removable covers shall be permitted to be laid flush with the floor surface. Such approved raceways shall be designed so that the cover plates provide adequate mechanical protection and rigidity equivalent to junction box covers.

(D) Other Raceways Flush With Concrete

In office occupancies, approved metal flat-top raceways, if not over 100 mm (4 in.) in width, shall be permitted to be laid flush with the concrete floor surface, provided they are covered with substantial linoleum that is not less than 1.6 mm (1/16 in.) thick or with equivalent floor covering. Where more than one and not more than three single raceways are each installed flush with the concrete, they shall be contiguous with each other and joined to form a rigid assembly.

390.20 Size of Conductors

No conductor larger than that for which the raceway is designed shall be installed in underfloor raceways.

390.22 Maximum Number of Conductors in Raceway

The combined cross-sectional area of all conductors or cables shall not exceed 40 percent of the interior cross-sectional area of the raceway.

390.23 Ampacity of Conductors

The ampacity adjustment factors in 310.15(C) shall apply to conductors installed in underfloor raceways.

390.56 Splices and Taps

Splices and taps shall be made only in junction boxes.

For the purposes of this section, so-called loop wiring (continuous, unbroken conductor connecting the individual outlets) shall not be considered to be a splice or tap.

Exception: Splices and taps shall be permitted in trench-type flush raceway having a removable cover that is accessible after installation. The conductors, including splices and taps, shall not fill more than 75 percent of the raceway area at that point.

390.57 Discontinued Outlets

When an outlet is abandoned, discontinued, or removed, the sections of circuit conductors supplying the outlet shall be removed from the raceway. No splices or reinsulated conductors, such as would be the case with abandoned outlets on loop wiring, shall be allowed in raceways.

390.70 Laid in Straight Lines

Underfloor raceways shall be laid so that a straight line from the center of one junction box to the center of the next junction box coincides with the centerline of the raceway system. Raceways shall be firmly held in place to prevent disturbing this alignment during construction.

390.71 Markers at Ends

A suitable marker shall be installed at or near each end of each straight run of raceways to locate the last insert.

390.73 Dead Ends

Dead ends of raceways shall be closed.

390.74 Junction Boxes

Junction boxes shall be leveled to the floor grade and sealed to prevent the free entrance of water or concrete. Junction boxes used with metal raceways shall be metal and shall be electrically continuous with the raceways.

390.75 Inserts

Inserts shall be leveled and sealed to prevent the entrance of concrete. Inserts used with metal raceways shall be metal and shall be electrically continuous with the raceway. Inserts set in or on fiber raceways before the floor is laid shall be mechanically secured to the raceway. Inserts set in fiber raceways after the floor is laid shall be screwed into the raceway. When cutting through the raceway wall and setting inserts, chips and other dirt shall not be allowed to remain in the raceway, and tools shall be used that are designed so as to prevent the tool from entering the raceway and damaging conductors that may be in place.

390.76 Connections to Cabinets and Wall Outlets

Connections from underfloor raceways to distribution centers and wall outlets shall be made by approved fittings or by any of the wiring methods in Chapter 3, where installed in accordance with the respective articles.

Article 392 Cable Trays

Part I General

392.1 Scope

This article covers cable tray systems, including ladder, ventilated trough, ventilated channel, solid bottom, and other similar structures.

Informational Note: For further information on cable trays, see ANSI/NEMA-VE 1-2017, Metal Cable Tray Systems, and NECA/NEMA 105-2015, Standard for Installing Metal Cable Tray Systems.

392.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Cable Tray System. A unit or assembly of units or sections and associated fittings forming a structural system used to securely fasten or support cables and raceways.

Part II Installation

392.10 Uses Permitted

Cable tray shall be permitted to be used as a support system for wiring methods containing service conductors, feeders, branch circuits, communications circuits, control circuits, and signaling circuits. Single insulated conductors shall be permitted in cable tray only when installed in accordance with 392.10(B)(1). Cable tray installations shall not be limited to industrial establishments. Where exposed to direct rays of the sun, insulated conductors and jacketed cables shall be identified as being sunlight resistant. Cable trays and their associated fittings shall be identified for the intended use.

(A) Wiring Methods

The wiring methods in Table 392.10(A) shall be permitted to be installed in cable tray systems under the conditions described in their respective articles and sections.

Table 392.10(A) Wiring Methods

Wiring Method Article

Armored cable: Type AC 320

CATV cables 820

Class 2 and Class 3 cables 725

Communications cables 800

Communications raceways 725, 770, and 800

Electrical metallic tubing: Type EMT 358

Electrical nonmetallic tubing: Type ENT 362

Fire alarm cables 760

Flexible metal conduit: Type FMC 348

Flexible metallic tubing: Type FMT 360

Instrumentation tray cable: Type ITC 727

Intermediate metal conduit: Type IMC 342

Liquidtight flexible metal conduit: Type LFMC 350

Liquidtight flexible nonmetallic conduit: Type LFNC 356

Metal-clad cable: Type MC 330

Mineral-insulated, metal-sheathed cable: Type MI 332

Network-powered broadband communications cables 830

Nonmetallic-sheathed cable: Types NM, NMC, and NMS 334

Non—power-limited fire alarm cable 760

Optical fiber cables 770

Other factory-assembled, multiconductor control, signal, or power cables that are specifically approved for installation in cable trays

Power and control tray cable: Type TC 336

Power-limited fire alarm cable 760

Power-limited tray cable 725

Rigid metal conduit: Type RMC 344

Rigid polyvinyl chloride conduit: Type PVC 352

Reinforced thermosetting resin conduit: Type RTRC 355

Service-entrance cable: Types SE and USE 338

Underground feeder and branch-circuit cable: Type UF 340

(B) In Industrial Establishments

The wiring methods in Table 392.10(A) shall be permitted to be used in any industrial establishment under the conditions described in their respective articles. In industrial establishments only, where conditions of maintenance and supervision ensure that only qualified persons service the installed cable tray system, any of the cables in 392.10(B)(1) and (B)(2) shall be permitted to be installed in ladder, ventilated trough, solid bottom, or ventilated channel cable trays.

(1) Single-Conductor Cables

Single-conductor cables shall be permitted to be installed in accordance with (B)(1)(a) through (B)(1)(c).

(a) Single-conductor cables shall be 1/0 AWG or larger and shall be of a type listed and marked on the surface for use in cable trays. Where 1/0 AWG through 4/0 AWG single-conductor cables are installed in ladder cable tray, the maximum allowable rung spacing for the ladder cable tray shall be 225 mm (9 in.).

(b) Welding cables shall comply with Article 630, Part IV.

(c) Single conductors used as equipment grounding conductors shall be insulated, covered, or bare, and they shall be 4 AWG or larger.

(2) Single- And Multiconductor Medium Voltage Cables

Single- and multiconductor medium voltage cables shall be Type MV cable. Single conductors shall be installed in accordance with 392.10(B)(1).

(C) Hazardous (Classified) Locations

Cable trays in hazardous (classified) locations shall contain only the cable types and raceways permitted by other articles in this Code.

(D) Nonmetallic Cable Tray

In addition to the uses permitted elsewhere in 392.10, nonmetallic cable tray shall be permitted in corrosive areas and in areas requiring voltage isolation.

(E) Airfield Lighting Cable Tray

In airports where maintenance and supervision conditions ensure that only qualified persons can access, install, or service the cable, airfield lighting cable used in series circuits that are rated up to 5000 volts and are powered by constant current regulators shall be permitted to be installed in cable trays.

Informational Note: Federal Aviation Administration (FAA) Advisory Circulars (ACs) provide additional practices and methods for airport lighting.

392.12 Uses Not Permitted

Cable tray systems shall not be used in hoistways or where subject to severe physical damage.

392.18 Cable Tray Installation

(A) Complete System

Cable trays shall be installed as a complete system. Field bends or modifications shall be so made that the electrical continuity of the cable tray system and support for the cables is maintained. Cable tray systems shall be permitted to have mechanically discontinuous segments between cable tray runs or between cable tray runs and equipment.

(B) Completed Before Installation

Each run of cable tray shall be completed before the installation of cables.

(C) Covers

In portions of runs where additional protection is required, covers or enclosures providing the required protection shall be of a material that is compatible with the cable tray.

(D) Through Partitions and Walls

Cable trays shall be permitted to extend transversely through partitions and walls or vertically through platforms and floors in wet or dry locations where the installations, complete with installed cables, are made in accordance with the requirements of 300.21.

(E) Exposed and Accessible

Cable trays shall be exposed and accessible, except as permitted by 392.18(D).

(F) Adequate Access

Sufficient space shall be provided and maintained about cable trays to permit adequate access for installing and maintaining the cables.

(G) Raceways, Cables, Boxes, and Conduit Bodies Supported From Cable Tray Systems

In industrial facilities where conditions of maintenance and supervision ensure that only qualified persons service the installation and where the cable tray systems are designed and installed to support the load, such systems shall be permitted to support raceways and cables, and boxes and conduit bodies covered in 314.1. For raceways terminating at the tray, a listed cable tray clamp or adapter shall be used to securely fasten the raceway to the cable tray system. Additional supporting and securing of the raceway shall be in accordance with the requirements of the appropriate raceway article. For raceways or cables running parallel to and attached to the bottom or side of a cable tray system, fastening and supporting shall be in accordance with the requirements of the appropriate raceway or cable article.

For boxes and conduit bodies attached to the bottom or side of a cable tray system, fastening and supporting shall be in accordance with the requirements of 314.23.

(H) Marking

Cable trays containing conductors operating over 600 volts shall have a permanent, legible warning notice carrying the wording "DANGER — HIGH VOLTAGE — KEEP AWAY" placed in a readily visible position on all cable trays, with the spacing of warning notices not to exceed 3 m (10 ft). The danger marking(s) or labels shall comply with 110.21(B).

Exception: Where not accessible (as applied to equipment), in industrial establishments where the conditions of maintenance and supervision ensure that only qualified persons service the installation, cable tray system warning notices shall be located where necessary for the installation to ensure safe maintenance and operation.

392.20 Cable and Conductor Installation

(A) Multiconductor Cables Operating at 1000 Volts or Less

Multiconductor cables operating at 1000 volts or less shall be permitted to be installed in the same tray.

(B) Cables Operating at Over 1000 Volts

Cables operating at over 1000 volts and those operating at 1000 volts or less installed in the same cable tray shall comply with either of the following:

The cables operating at over 1000 volts are Type MC.

The cables operating at over 1000 volts are separated from the cables operating at 1000 volts or less by a solid fixed barrier of a material compatible with the cable tray.

(C) Connected in Parallel

Where single conductor cables comprising each phase, neutral, or grounded conductor of an alternating-current circuit are connected in parallel as permitted in 310.10(G), the conductors shall be installed in groups consisting of not more than one conductor per phase, neutral, or grounded conductor to prevent current imbalance in the paralleled conductors due to inductive reactance.

Single conductors shall be securely bound in circuit groups to prevent excessive movement due to fault-current magnetic forces unless single conductors are cabled together, such as triplexed assemblies.

(D) Single Conductors

Where any of the single conductors installed in ladder or ventilated trough cable trays are 1/0 through 4/0 AWG, all single conductors shall be installed in a single layer. Conductors that are bound together to comprise each circuit group shall be permitted to be installed in other than a single layer.

392.22 Number of Conductors or Cables

(A) Number of Multiconductor Cables, Rated 2000 Volts or Less, in Cable Trays

The number of multiconductor cables, rated 2000 volts or less, permitted in a single cable tray shall not exceed the requirements of this section. The conductor sizes shall apply to both aluminum and copper conductors. Where dividers are used, fill calculations shall apply to each divided section of the cable tray.

Table 392.22(A) Allowable Cable Fill Area for Multiconductor Cables in Ladder, Ventilated Trough, or Solid Bottom Cable Trays for Cables Rated 2000 Volts or Less

Inside Width of Cable Tray Maximum Allowable Fill Area for Multiconductor Cables

Ladder or Ventilated Trough or Wire Mesh Cable Trays, 392.22(A)(1) Solid Bottom Cable Trays, 392.22(A)(3)

Column 1 Applicable for 392.22(A)(1)(b) Only Column 2a Applicable for 392.22(A)(1)(c) Only Column 3 Applicable for 392.22(A)(3)(b) Only Column 4a Applicable for 392.22(A)(3)(c) Only

mm in. mm2 in.2 mm2 in.2 mm2 in.2 mm2 in.2

50 2.0 1,500 2.5 1,500 — (30 Sd)b 2.5 — (1.2 Sd)b 1,200 2.0 1,200 — (25 Sd)b 2.0 — Sdb

100 4.0 3,000 4.5 3,000 — (30 Sd)b 4.5 — (1.2 Sd) 2,300 3.5 2,300 — (25 Sd) 3.5 — Sd

150 6.0 4,500 7.0 4,500 — (30 Sd)b 7 — (1.2 Sd) 3,500 5.5 3,500 — (25 Sd)b 5.5—Sd

200 8.0 6,000 9.5 6,000 — (30 Sd)b 9.5 — (1.2 Sd) 4,500 7.0 4,500 — (25 Sd) 7.0 — Sd

225 9.0 6,800 10.5 6,800 — (30 Sd) 10.5 — (1.2 Sd) 5,100 8.0 5,100 — (25 Sd) 8.0 — Sd

300 12.0 9,000 14.0 9,000 — (30 Sd) 14 — (1.2 Sd) 7,100 11.0 7,100 — (25 Sd) 11.0 — Sd

400 16.0 12,000 18.5 12,000 — (30 Sd) 18.5 — (1.2 Sd) 9,400 14.5 9,400 — (25 Sd) 14.5 — Sd

450 18.0 13,500 21.0 13,500 — (30 Sd) 21 — (1.2 Sd) 10,600 16.5 10,600 — (25 Sd) 16.5 — Sd

500 20.0 15,000 23.5 15,000 — (30 Sd) 23.5 — (1.2 Sd) 11,800 18.5 11,800 — (25 Sd) 18.5 — Sd

600 24.0 18,000 28.0 18,000 — (30 Sd) 28 — (1.2 Sd) 14,200 22.0 14,200 — (25 Sd) 22.0 — Sd

750 30.0 22,500 35.0 22,500 — (30 Sd) 35 — (1.2 Sd) 17,700 27.5 17,700 — (25 Sd) 27.5 — Sd

900 36.0 27,000 42.0 27,000 — (30 Sd) 42 — (1.2 Sd) 21,300 33.0 21,300 — (25 Sd) 33.0 — Sd

aThe maximum allowable fill areas in Columns 2 and 4 shall be calculated. For example, the maximum allowable fill in mm2 for a 150-mm wide cable tray in Column 2 shall be 4500 minus (30 multiplied by Sd) [the maximum allowable fill, in square inches, for a 6-in. wide cable tray in Column 2 shall be 7 minus (1.2 multiplied by Sd)].

bThe term Sd in Columns 2 and 4 is equal to the sum of the diameters, in mm, of all cables 107.2 mm (in inches, of all 4/0 AWG) and larger multiconductor cables in the same cable tray with smaller cables.

(1) Ladder or Ventilated Trough Cable Trays Containing Any Mixture of Cables

Where ladder or ventilated trough cable trays contain multiconductor power or lighting cables, or any mixture of multiconductor power, lighting, control, and signal cables, the maximum number of cables shall conform to the following:

(a) Where all of the cables are 4/0 AWG or larger, the sum of the diameters of all cables shall not exceed the cable tray width, and the cables shall be installed in a single layer. Where the cable ampacity is determined according to 392.80(A)(1)(c), the cable tray width shall not be less than the sum of the diameters of the cables and the sum of the required spacing widths between the cables.

(b) Where all of the cables are smaller than 4/0 AWG, the sum of the cross-sectional areas of all cables shall not exceed the maximum allowable cable fill area in Column 1 of Table 392.22(A) for the appropriate cable tray width.

(c) Where 4/0 AWG or larger cables are installed in the same cable tray with cables smaller than 4/0 AWG, the sum of the cross-sectional areas of all cables smaller than 4/0 AWG shall not exceed the maximum allowable fill area resulting from the calculation in Column 2 of Table 392.22(A) for the appropriate cable tray width. The 4/0 AWG and larger cables shall be installed in a single layer, and no other cables shall be placed on them.

(2) Ladder or Ventilated Trough Cable Trays Containing Multiconductor Control and/or Signal Cables Only

Where a ladder or ventilated trough cable tray having a usable inside depth of 150 mm (6 in.) or less contains multiconductor control and/or signal cables only, the sum of the cross-sectional areas of all cables at any cross section shall not exceed 50 percent of the interior cross-sectional area of the cable tray. A depth of 150 mm (6 in.) shall be used to calculate the allowable interior cross-sectional area of any cable tray that has a usable inside depth of more than 150 mm (6 in.).

(3) Solid Bottom Cable Trays Containing Any Mixture of Cables

Where solid bottom cable trays contain multiconductor power or lighting cables, or any mixture of multiconductor power, lighting, control, and signal cables, the maximum number of cables shall conform to the following:

(a) Where all of the cables are 4/0 AWG or larger, the sum of the diameters of all cables shall not exceed 90 percent of the cable tray width, and the cables shall be installed in a single layer.

(b) Where all of the cables are smaller than 4/0 AWG, the sum of the cross-sectional areas of all cables shall not exceed the maximum allowable cable fill area in Column 3 of Table 392.22(A) for the appropriate cable tray width.

(c) Where 4/0 AWG or larger cables are installed in the same cable tray with cables smaller than 4/0 AWG, the sum of the cross-sectional areas of all cables smaller than 4/0 AWG shall not exceed the maximum allowable fill area resulting from the computation in Column 4 of Table 392.22(A) for the appropriate cable tray width. The 4/0 AWG and larger cables shall be installed in a single layer, and no other cables shall be placed on them.

(4) Solid Bottom Cable Tray Containing Multiconductor Control and/or Signal Cables Only

Where a solid bottom cable tray having a usable inside depth of 150 mm (6 in.) or less contains multiconductor control and/or signal cables only, the sum of the cross sectional areas of all cables at any cross section shall not exceed 40 percent of the interior cross-sectional area of the cable tray. A depth of 150 mm (6 in.) shall be used to calculate the allowable interior cross-sectional area of any cable tray that has a usable inside depth of more than 150 mm (6 in.).

(5) Ventilated Channel Cable Trays Containing Multiconductor Cables of Any Type

Where ventilated channel cable trays contain multiconductor cables of any type, the following shall apply:

(a) Where only one multiconductor cable is installed, the cross-sectional area shall not exceed the value specified in Column 1 of Table 392.22(A)(5).

(b) Where more than one multiconductor cable is installed, the sum of the cross-sectional area of all cables shall not exceed the value specified in Column 2 of Table 392.22(A)(5).

Table 392.22(A)(5) Allowable Cable Fill Area for Multiconductor Cables in Ventilated Channel Cable Trays for Cables Rated 2000 Volts or Less

Inside Width of Cable Tray Maximum Allowable Fill Area for Multiconductor Cables

Column 1 One Cable Column 2 More Than One Cable

mm in. mm2 in.2 mm2 in.2

75 3 1500 2.3 850 1.3

100 4 2900 4.5 1600 2.5

150 6 4500 7.0 2450 3.8

(6) Solid Channel Cable Trays Containing Multiconductor Cables of Any Type

Where solid channel cable trays contain multiconductor cables of any type, the following shall apply:

(a) Where only one multiconductor cable is installed, the cross-sectional area of the cable shall not exceed the value specified in Column 1 of Table 392.22(A)(6).

(b) Where more than one multiconductor cable is installed, the sum of the cross-sectional area of all cable shall not exceed the value specified in Column 2 of Table 392.22(A)(6).

Table 392.22(A)(6) Allowable Cable Fill Area for Multiconductor Cables in Solid Channel Cable Trays for Cables Rated 2000 Volts or Less

Inside Width of Cable Tray Column 1 One Cable Column 2 More Than One Cable

mm in. mm2 in.2 mm2 in.2

50 2 850 1.3 500 0.8

75 3 1300 2.0 700 1.1

100 4 2400 3.7 1400 2.1

150 6 3600 5.5 2100 3.2

(B) Number of Single-Conductor Cables, Rated 2000 Volts or Less, in Cable Trays

The number of single conductor cables, rated 2000 volts or less, permitted in a single cable tray section shall not exceed the requirements of this section. The single conductors, or conductor assemblies, shall be evenly distributed across the cable tray. The conductor sizes shall apply to both aluminum and copper conductors.

(1) Ladder or Ventilated Trough Cable Trays

Where ladder or ventilated trough cable trays contain single-conductor cables, the maximum number of single conductors shall conform to the following:

(a) Where all of the cables are 1000 kcmil or larger, the sum of the diameters of all single-conductor cables shall not exceed the cable tray width, and the cables shall be installed in a single layer. Conductors that are bound together to comprise each circuit group shall be permitted to be installed in other than a single layer.

(b) Where all of the cables are from 250 kcmil through 900 kcmil, the sum of the cross-sectional areas of all single-conductor cables shall not exceed the maximum allowable cable fill area in Column 1 of Table 392.22(B)(1) for the appropriate cable tray width.

(c) Where 1000 kcmil or larger single-conductor cables are installed in the same cable tray with single-conductor cables smaller than 1000 kcmil, the sum of the cross sectional areas of all cables smaller than 1000 kcmil shall not exceed the maximum allowable fill area resulting from the computation in Column 2 of Table 392.22(B)(1) for the appropriate cable tray width.

(d) Where any of the single conductor cables are 1/0 through 4/0 AWG, the sum of the diameters of all single conductor cables shall not exceed the cable tray width.

Table 392.22(B)(1) Allowable Cable Fill Area for Single-Conductor Cables in Ladder, Ventilated Trough, or Wire Mesh Cable Trays for Cables Rated 2000 Volts or Less

Inside Width of Cable Tray Maximum Allowable Fill Area for Single-Conductor Cables in Ladder, Ventilated Trough, or Wire Mesh Cable Trays

Column 1 Applicable for 392.22(B)(1)(b) Only Column 2a Applicable for 392.22(B)(1)(c) Only

mm in. mm2 in.2 mm2 in.2

50 2 1,400 2.0 1,400 — (28 Sd)b 2.0 — (1.1 Sd)b

100 4 2,800 4.5 2,800 — (28 Sd) 4.5 — (1.1 Sd)

150 6 4,200 6.5 4,200 — (28 Sd)b 6.5 — (1.1 Sd)b

200 8 5,600 8.5 5,600 — (28 Sd) 8.5 — (1.1 Sd)

225 9 6,100 9.5 6,100 — (28 Sd) 9.5 — (1.1 Sd)

300 12 8,400 13.0 8,400 — (28 Sd) 13.0 — (1.1 Sd)

400 16 11,200 17.5 11,200 — (28 Sd) 17.5 — (1.1 Sd)

450 18 12,600 19.5 12,600 — (28 Sd) 19.5 — (1.1 Sd)

500 20 14,000 21.5 14,000 — (28 Sd) 21.5 — (1.1 Sd)

600 24 16,800 26.0 16,800 — (28 Sd) 26.0 — (1.1 Sd)

750 30 21,000 32.5 21,000 — (28 Sd) 32.5 — (1.1 Sd)

900 36 25,200 39.0 25,200 — (28 Sd) 39.0 — (1.1 Sd)

aThe maximum allowable fill areas in Column 2 shall be calculated. For example, the maximum allowable fill, in mm2, for a 150-mm wide cable tray in Column 2 shall be 4200 minus (28 multiplied by Sd) [the maximum allowable fill, in square inches, for a 6-in. wide cable tray in Column 2 shall be 6.5 minus (1.1 multiplied by Sd)].

bThe term Sd in Column 2 is equal to the sum of the diameters, in mm, of all cables 507 mm2 (in inches, of all 1000 kcmil) and larger single-conductor cables in the same cable tray with small cables.

(2) Ventilated Channel Cable Trays

Where 50 mm (2 in.), 75 mm (3 in.), 100 mm (4 in.), or 150 mm (6 in.) wide ventilated channel cable trays contain single-conductor cables, the sum of the diameters of all single conductors shall not exceed the inside width of the channel.

(C) Number of Type MV and Type MC Cables (2001 Volts or Over) in Cable Trays

The number of cables rated 2001 volts or over permitted in a single cable tray shall not exceed the requirements of this section.

The sum of the diameters of single-conductor and multiconductor cables shall not exceed the cable tray width, and the cables shall be installed in a single layer. Where single conductor cables are triplexed, quadruplexed, or bound together in circuit groups, the sum of the diameters of the single conductors shall not exceed the cable tray width, and these groups shall be installed in single layer arrangement.

392.30 Securing and Supporting

(A) Cable Trays

Cable trays shall be supported at intervals in accordance with the installation instructions.

(B) Cables and Conductors

Cables and conductors shall be secured to and supported by the cable tray system in accordance with (1), (2), (3), and (4) as applicable:

In other than horizontal runs, the cables shall be fastened securely to transverse members of the cable tray.

Supports shall be provided to prevent stress on cables where they enter raceways from cable tray systems.

The system shall provide for the support of cables and raceway wiring methods in accordance with their corresponding articles. Where cable trays support individual conductors or multiconductor cables and where the conductors or multiconductor cables pass from one cable tray to another, or from a cable tray to raceway(s) or from a cable tray to equipment where the conductors are terminated, the distance between the cable trays or between the cable tray and the raceway(s) or the equipment shall not exceed 1.8 m (6 ft). The conductors shall be secured to the cable tray(s) at the transition, and they shall be protected, by guarding or by location, from physical damage.

Cable ties shall be listed and identified for the application and for securement and support.

392.44 Expansion Splice Plates

Expansion splice plates for cable trays shall be provided where necessary to compensate for thermal expansion and contraction.

392.46 Bushed Conduit and Tubing

A box shall not be required where cables or conductors are installed in bushed conduit and tubing used for support or for protection against physical damage or where conductors or cables transition to a raceway wiring method from the cable tray. Conductors shall be permitted to enter equipment in accordance with 392.46(A) or (B).

(A) Through Bushed Conduit or Tubing

Individual conductors or multiconductor cables with entirely nonmetallic sheaths shall be permitted to enter enclosures where they are terminated through nonflexible bushed conduit or tubing installed for their protection provided they are secured at the point of transition from the cable tray and the conduit or tubing is sealed at the outer end using an approved means so as to prevent debris from entering the equipment through the conduit or tubing.

(B) Flanged Connections

Individual conductors or multiconductor cables with entirely nonmetallic sheaths shall be permitted to enter enclosures through openings associated with flanges from cable trays where the cable tray is attached to the flange and the flange is mounted directly to the equipment. The openings shall be made such that the conductors are protected from abrasion and the opening shall be sealed or covered to prevent debris from entering the enclosure through the opening.

Informational Note: One method of preventing debris from entering the enclosure is to seal the outer end of the raceway or the opening with duct seal.

392.56 Cable Splices

Cable splices made and insulated by approved methods shall be permitted to be located within a cable tray, provided they are accessible. Splices shall be permitted to project above the side rails where not subject to physical damage.

392.60 Grounding and Bonding

(A) Metal Cable Trays

Metal cable trays shall be permitted to be used as equipment grounding conductors where continuous maintenance and supervision ensure that qualified persons service the installed cable tray system and the cable tray complies with this section. Metal cable trays that support electrical conductors shall be grounded as required for conductor enclosures in accordance with 250.96 and Part IV of Article 250. Metal cable trays containing only non-power conductors shall be electrically continuous through approved connections or the use of a bonding jumper.

Informational Note: Examples of non-power conductors include nonconductive optical fiber cables and Class 2 and Class 3 remote-control, signaling, and power-limited circuits.

(B) Steel or Aluminum Cable Tray Systems

Steel or aluminum cable tray systems shall be permitted to be used as equipment grounding conductors, provided all the following requirements are met:

The cable tray sections and fittings are identified as an equipment grounding conductor.

The minimum cross-sectional area of cable trays conform to the requirements in Table 392.60(B).

All cable tray sections and fittings are legibly and durably marked to show the cross-sectional area of metal in channel cable trays, or cable trays of one-piece construction, and the total cross-sectional area of both side rails for ladder or trough cable trays.

Cable tray sections, fittings, and connected raceways are bonded in accordance with 250.96, using bolted mechanical connectors or bonding jumpers sized and installed in accordance with 250.102.

Table 392.60(B) Metal Area Requirements for Cable Trays Used as Equipment Grounding Conductor

Maximum Fuse Ampere Rating, Circuit Breaker Ampere Trip Setting, or Circuit Breaker Protective Relay Ampere Trip Setting for Ground-Fault Protection of Any Cable Circuit in the Cable Tray System Minimum Cross-Sectional Area of Metal\*

Steel Cable Trays Aluminum Cable Trays

mm2 in.2 mm2 in.2

60 129 0.20 129 0.20

100 258 0.40 129 0.20

200 451.5 0.70 129 0.20

400 645 1.00 258 0.40

600 967.5 1.50† 258 0.40

1000 — — 387 0.60

1200 — — 645 1.00

1600 — — 967.5 1.50

2000 — — 1290 2.00†

\*Total cross-sectional area of both side rails for ladder or trough cable trays; or the minimum cross-sectional area of metal in channel cable trays or cable trays of one-piece construction.

†Steel cable trays shall not be used as equipment grounding conductors for circuits with ground-fault protection above 600 amperes. Aluminum cable trays shall not be used as equipment grounding conductors for circuits with ground-fault protection above 2000 amperes.

(C) Transitions

Where metal cable tray systems are mechanically discontinuous, as permitted in 392.18(A), a bonding jumper sized in accordance with 250.102 shall connect the two sections of the cable tray, or the cable tray and the raceway or equipment. Bonding shall be in accordance with 250.96.

392.80 Ampacity of Conductors

(A) Ampacity of Cables, Rated 2000 Volts or Less, in Cable Trays

Informational Note: See 110.14(C) for conductor temperature limitations due to termination provisions.

(1) Multiconductor Cables

The ampacity of multiconductor cables, nominally rated 2000 volts or less, installed according to the requirements of 392.22(A) shall be as given in Table 310.16 and Table 310.18, subject to 392.80(A)(1)(a), (A)(1)(b), (A)(1)(c), and 310.14(A)(2).

(a) The adjustment factors of 310.15(C)(1) shall apply only to multiconductor cables with more than three current-carrying conductors. Adjustment factors shall be limited to the number of current-carrying conductors in the cable and not to the number of conductors in the cable tray.

(b) Where cable trays are continuously covered for more than 1.8 m (6 ft) with solid unventilated covers, not over 95 percent of the ampacities of Table 310.16 and Table 310.18 shall be permitted for multiconductor cables.

(c) Where multiconductor cables are installed in a single layer in uncovered trays, with a maintained spacing of not less than one cable diameter between cables, the ampacity shall not exceed the ambient temperature-corrected ampacities of multiconductor cables, with not more than three insulated conductors rated 0 through 2000 volts in free air, in accordance with 310.14(B).

Informational Note: See Informative Annex B, Table B.2(3).

(2) Single-Conductor Cables

The ampacity of single-conductor cables shall be as permitted by 310.14(A)(2). The adjustment factors of 310.15(C)(1) shall not apply to the ampacity of cables in cable trays. The ampacity of single-conductor cables, or single conductors cabled together (triplexed, quadruplexed, and so forth), nominally rated 2000 volts or less, shall comply with the following:

(a) Where installed according to the requirements of 392.22(B), the ampacities for 600 kcmil and larger single-conductor cables in uncovered cable trays shall not exceed 75 percent of the ampacities in Table 310.17 and Table 310.19. Where cable trays are continuously covered for more than 1.8 m (6 ft) with solid unventilated covers, the ampacities for 600 kcmil and larger cables shall not exceed 70 percent of the ampacities in Table 310.17 and Table 310.19.

(b) Where installed according to the requirements of 392.22(B), the ampacities for 1/0 AWG through 500 kcmil single-conductor cables in uncovered cable trays shall not exceed 65 percent of the ampacities in Table 310.17 and Table 310.19. Where cable trays are continuously covered for more than 1.8 m (6 ft) with solid unventilated covers, the ampacities for 1/0 AWG through 500 kcmil cables shall not exceed 60 percent of the ampacities in Table 310.17 and Table 310.19.

(c) Where single conductors are installed in a single layer in uncovered cable trays, with a maintained space of not less than one cable diameter between individual conductors, the ampacity of 1/0 AWG and larger cables shall not exceed the ampacities in Table 310.17 and Table 310.19.

Exception to (2)(c): For solid bottom cable trays, the ampacity of single conductor cables shall be determined by 310.14(B).

(d) Where single conductors are installed in a triangular or square configuration in uncovered cable trays, with a maintained free airspace of not less than 2.15 times one conductor diameter (2.15 × O.D.) of the largest conductor contained within the configuration and adjacent conductor configurations or cables, the ampacity of 1/0 AWG and larger cables shall not exceed the ampacities of two or three single insulated conductors rated 0 through 2000 volts supported on a messenger in accordance with 310.15.

Informational Note: See Table 310.20.

(3) Combinations of Multiconductor and Single-Conductor Cables

Where a cable tray contains a combination of multiconductor and single-conductor cables, the ampacities shall be as given in 392.80(A)(1) for multiconductor cables and 392.80(A)(2) for single-conductor cables, provided that the following conditions apply:

The sum of the multiconductor cable fill area as a percentage of the allowable fill area for the tray calculated in accordance with 392.22(A), and the single-conductor cable fill area as a percentage of the allowable fill area for the tray calculated in accordance with 392.22(B), totals not more than 100 percent.

Multiconductor cables are installed according to 392.22(A), and single-conductor cables are installed according to 392.22(B) and 392.22(C).

(B) Ampacity of Type MV and Type MC Cables (2001 Volts or Over) in Cable Trays

The ampacity of cables, rated 2001 volts, nominal, or over, installed according to 392.22(C) shall not exceed the requirements of this section.

Informational Note: See 110.40 for conductor temperature limitations due to termination provisions.

(1) Multiconductor Cables (2001 Volts or Over)

The ampacity of multiconductor cables shall be as given in Table 311.60(C)(75) and Table 311.60(C)(76), subject to the following:

Where cable trays are continuously covered for more than 1.8 m (6 ft) with solid unventilated covers, not more than 95 percent of the ampacities of Table 311.60(C)(75) and Table 311.60(C)(76) shall be permitted for multiconductor cables.

Where multiconductor cables are installed in a single layer in uncovered cable trays, with maintained spacing of not less than one cable diameter between cables, the ampacity shall not exceed the allowable ampacities of Table 311.60(C)(71) and Table 311.60(C)(72).

(2) Single-Conductor Cables (2001 Volts or Over)

The ampacity of single-conductor cables, or single conductors cabled together (triplexed, quadruplexed, and so forth), shall comply with the following:

The ampacities for 1/0 AWG and larger single-conductor cables in uncovered cable trays shall not exceed 75 percent of the ampacities in Table 311.60(C)(69) and Table 311.60(C)(70). Where the cable trays are covered for more than 1.8 m (6 ft) with solid unventilated covers, the ampacities for 1/0 AWG and larger single-conductor cables shall not exceed 70 percent of the ampacities in Table 311.60(C)(69) and Table 311.60(C)(70).

Where single-conductor cables are installed in a single layer in uncovered cable trays, with a maintained space of not less than one cable diameter between individual conductors, the ampacity of 1/0 AWG and larger cables shall not exceed the ampacities in Table 311.60(C)(69) and Table 311.60(C)(70).

Where single conductors are installed in a triangular or square configuration in uncovered cable trays, with a maintained free air space of not less than 2.15 times the diameter (2.15 × O.D.) of the largest conductor contained within the configuration and adjacent conductor configurations or cables, the ampacity of 1/0 AWG and larger cables shall not exceed the ampacities in Table 311.60(C)(67) and Table 311.60(C)(68).

Part III Construction Specifications

392.100 Construction

(A) Strength and Rigidity

Cable trays shall have suitable strength and rigidity to provide adequate support for all contained wiring.

(B) Smooth Edges

Cable trays shall not have sharp edges, burrs, or projections that could damage the insulation or jackets of the wiring.

(C) Corrosion Protection

Cable tray systems shall be corrosion resistant. If made of ferrous material, the system shall be protected from corrosion as required by 300.6.

(D) Side Rails

Cable trays shall have side rails or equivalent structural members.

(E) Fittings

Cable trays shall include fittings or other suitable means for changes in direction and elevation of runs.

(F) Nonmetallic Cable Tray

Nonmetallic cable trays shall be made of flame-retardant material.

Article 393 Low-Voltage Suspended Ceiling Power Distribution Systems

Part I General

393.1 Scope

This article covers the installation of low-voltage suspended ceiling power distribution systems.

393.2 Definitions

The definitions in this section shall apply only within this article.

Busbar. A noninsulated conductor electrically connected to the source of supply and physically supported on an insulator providing a power rail for connection to utilization equipment, such as sensors, actuators, A/V devices, low-voltage luminaire assemblies, and similar electrical equipment.

Busbar Support. An insulator that runs the length of a section of suspended ceiling bus rail that serves to support and isolate the busbars from the suspended grid rail.

Connector. A term used to refer to an electromechanical fitting.

Connector, Load. An electromechanical connector used for power from the busbar to utilization equipment.

Connector, Pendant. An electromechanical or mechanical connector used to suspend low-voltage luminaire or utilization equipment below the grid rail and to supply power to connect from the busbar to utilization equipment.

Connector, Power Feed. An electromechanical connector used to connect the power supply to a power distribution cable, to connect directly to the busbar, or to connect from a power distribution cable to the busbar.

Connector, Rail to Rail. An electromechanical connector used to interconnect busbars from one ceiling grid rail to another grid rail.

Grid Bus Rail. A combination of the busbar, the busbar support, and the structural suspended ceiling grid system.

Low-Voltage Suspended Ceiling Power Distribution System. A system that serves as a support for a finished ceiling surface and consists of a busbar and busbar support system to distribute power to utilization equipment supplied by a Class 2 power supply.

Power Supply. A Class 2 power supply connected between the branch-circuit power distribution system and the busbar low-voltage suspended ceiling power distribution system.

Rail. The structural support for the suspended ceiling system typically forming the ceiling grid supporting the ceiling tile and listed utilization equipment, such as sensors, actuators, A/V devices, and low-voltage luminaires and similar electrical equipment.

Reverse Polarity Protection (Backfeed Protection). A system that prevents two interconnected power supplies, connected positive to negative, from passing current from one power source into a second power source.

Suspended Ceiling Grid. A system that serves as a support for a finished ceiling surface and other utilization equipment.

393.6 Listing Requirements

Suspended ceiling power distribution systems and associated fittings shall be listed as in 393.6(A) or (B).

(A) Listed System

Low-voltage suspended ceiling distribution systems operating at 30 volts ac or less or 60 volts dc or less shall be listed as a complete system, with the utilization equipment, power supply, and fittings as part of the same identified system.

(B) Assembly of Listed Parts

A low-voltage suspended ceiling power distribution system assembled from the following parts, listed according to the appropriate function, shall be permitted:

Listed low-voltage utilization equipment

Listed Class 2 power supply

Listed or identified fittings, including connectors and grid rails with bare conductors

Listed low-voltage cables in accordance with 725.179, conductors in raceways, or other fixed wiring methods for the secondary circuit

Part II Installation

393.10 Uses Permitted

Low-voltage suspended ceiling power distribution systems shall be permanently connected and shall be permitted as follows:

For listed utilization equipment capable of operation at a maximum of 30 volts ac (42.4 volts peak) or 60 volts dc (24.8 volts peak for dc interrupted at a rate of 10 Hz to 200 Hz) and limited to Class 2 power levels in Chapter 9, Table 11(A) and Table 11(B) for lighting, control, and signaling circuits.

In indoor dry locations.

For residential, commercial, and industrial installations.

In other spaces used for environmental air in accordance with 300.22(C), electrical equipment having a metal enclosure, or with a nonmetallic enclosure and fittings, shall be listed for use within an air-handling space and shall have adequate fire-resistant and low-smoke-producing characteristics and associated wiring material suitable for the ambient temperature.

Informational Note: One method of defining adequate fire-resistant and low-smoke-producing characteristics for electrical equipment with a nonmetallic enclosure is in ANSI/UL 2043-2013, Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces.

393.12 Uses Not Permitted

Suspended ceiling power distribution systems shall not be installed in the following:

In damp or wet locations

Where subject to corrosive fumes or vapors, such as storage battery rooms

Where subject to physical damage

In concealed locations

In hazardous (classified) locations

As part of a fire-rated floor-ceiling or roof-ceiling assembly, unless specifically listed as part of the assembly

For lighting in general or critical patient care areas

393.14 Installation

(A) General Requirements

Support wiring shall be installed in a neat and workmanlike manner. Cables and conductors installed exposed on the surface of ceilings and sidewalls shall be supported by the building structure in such a manner that the cable is not damaged by normal building use. Such cables shall be supported by straps, staples, hangers, cable ties listed and identified for securement and support, or similar fittings designed and installed so as not to damage the cable.

Informational Note: Suspended ceiling low-voltage power grid distribution systems should be installed by qualified persons in accordance with the manufacturer's installation instructions.

(B) Insulated Conductors

Exposed insulated secondary circuit conductors shall be listed, of the type, and installed as described as follows:

Class 2 cable supplied by a listed Class 2 power source and installed in accordance with Parts I and III of Article 725

Wiring methods described in Chapter 3

393.21 Disconnecting Means

(A) Location

A disconnecting means for the Class 2 supply to the power grid system shall be located so as to be accessible and within sight of the Class 2 power source for servicing or maintenance of the grid system.

(B) Multiwire Branch Circuits

Where connected to a multiwire branch circuit, the disconnecting means shall simultaneously disconnect all the supply conductors, including the grounded conductors.

393.30 Securing and Supporting

(A) Attached to Building Structure

A suspended ceiling low-voltage power distribution system shall be secured to the mounting surface of the building structure by hanging wires, screws, or bolts in accordance with the installation and operation instructions. Mounting hardware, such as screws or bolts, shall be either packaged with the suspended ceiling low-voltage lighting power distribution system, or the installation instructions shall specify the types of mounting fasteners to be used.

(B) Attachment of Power Grid Rails

The individual power grid rails shall be mechanically secured to the overall ceiling grid assembly.

393.40 Connectors and Enclosures

(A) Connectors

Connections to busbar grid rails, cables, and conductors shall be made with listed insulating devices, and these connections shall be accessible after installation. A soldered connection shall be made mechanically secure before being soldered. Other means of securing leads, such as push-on terminals and spade-type connectors, shall provide a secure mechanical connection. The following connectors shall be permitted to be used as connection or interconnection devices:

Load connectors shall be used for power from the busbar to listed utilization equipment.

A pendant connector shall be permitted to suspend low-voltage luminaires or utilization equipment below the grid rail and to supply power from the busbar to the utilization equipment.

A power feed connector shall be permitted to connect the power supply directly to a power distribution cable and to the busbar.

Rail-to-rail connectors shall be permitted to interconnect busbars from one ceiling grid rail to another grid rail.

Informational Note: For quick-connect terminals, see UL 310, Standard for Electrical Quick-Connect, and for mechanical splicing devices, see UL 486A-486B, Standard for Wire Connectors.

(B) Enclosures

Where made in a wall, connections shall be installed in an enclosure in accordance with Parts I, II, and III of Article 314.

393.45 Overcurrent and Reverse Polarity (Backfeed) Protection

(A) Overcurrent Protection

The listed Class 2 power supply or transformer primary shall be protected at not greater than 20 amperes.

(B) Interconnection of Power Sources

Listed Class 2 sources shall not have the output connections paralleled or otherwise interconnected unless listed for such interconnection.

(C) Reverse Polarity (Backfeed) Protection of Direct-Current Systems

A suspended ceiling low-voltage power distribution system shall be permitted to have reverse polarity (backfeed) protection of dc circuits by one of the following means:

If the power supply is provided as part of the system, the power supply is provided with reverse polarity (backfeed) protection; or

If the power supply is not provided as part of the system, reverse polarity or backfeed protection can be provided as part of the grid rail busbar or as a part of the power feed connector.

393.56 Splices

A busbar splice shall be provided with insulation and mechanical protection equivalent to that of the grid rail busbars involved.

393.57 Connections

Connections in busbar grid rails, cables, and conductors shall be made with listed insulating devices and be accessible after installation. Where made in a wall, connections shall be installed in an enclosure in accordance with Parts I, II, and III of Article 314, as applicable.

393.60 Grounding

(A) Grounding of Supply Side of Class 2 Power Source

The supply side of the Class 2 power source shall be connected to an equipment grounding conductor in accordance with the applicable requirements in Part IV of Article 250.

(B) Grounding of Load Side of Class 2 Power Source

Class 2 load side circuits for suspended ceiling low-voltage power grid distribution systems shall not be grounded.

Part III Construction Specifications

393.104 Sizes and Types of Conductors

(A) Load Side Utilization Conductor Size

Current-carrying conductors for load side utilization equipment shall be copper and shall be 18 AWG minimum.

Exception: Conductors of a size smaller than 18 AWG, but not smaller than 24 AWG, shall be permitted to be used for Class 2 circuits. Where used, these conductors shall be installed using a Chapter 3 wiring method, shall be totally enclosed, shall not be subject to movement or strain, and shall comply with the ampacity requirements in Table 522.22.

(B) Power Feed Bus Rail Conductor Size

The power feed bus rail shall be 16 AWG minimum or equivalent. For a busbar with a circular cross section, the diameter shall be 1.29 mm (0.051 in.) minimum, and, for other than circular busbars, the area shall be 1.32 mm2 (0.002 in.2) minimum.

Article 394 Concealed Knob-and-Tube Wiring

Part I General

394.1 Scope

This article covers the use, installation, and construction specifications of concealed knob-and-tube wiring.

394.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Concealed Knob-and-Tube Wiring. A wiring method using knobs, tubes, and flexible nonmetallic tubing for the protection and support of single insulated conductors.

Part II Installation

394.10 Uses Permitted

Concealed knob-and-tube wiring shall be permitted to be installed in the hollow spaces of walls and ceilings, or in unfinished attics and roof spaces as provided by 394.23, only as follows:

For extensions of existing installations

Elsewhere by special permission

394.12 Uses Not Permitted

Concealed knob-and-tube wiring shall not be used in the following:

Commercial garages

Theaters and similar locations

Motion picture studios

Hazardous (classified) locations

Hollow spaces of walls, ceilings, and attics where such spaces are insulated by loose, rolled, or foamed-in-place insulating material that envelops the conductors

394.17 Through or Parallel to Framing Members

Conductors shall comply with 398.17 where passing through holes in structural members. Where passing through wood cross members in plastered partitions, conductors shall be protected by noncombustible, nonabsorbent, insulating tubes extending not less than 75 mm (3 in.) beyond the wood member.

394.19 Clearances

(A) General

A clearance of not less than 75 mm (3 in.) shall be maintained between conductors and a clearance of not less than 25 mm (1 in.) between the conductor and the surface over which it passes.

(B) Limited Conductor Space

Where space is too limited to provide these minimum clearances, such as at meters, panelboards, outlets, and switch points, the individual conductors shall be enclosed in flexible nonmetallic tubing, which shall be continuous in length between the last support and the enclosure or terminal point.

(C) Clearance From Piping, Exposed Conductors, and So Forth

Conductors shall comply with 398.19 for clearances from other exposed conductors, piping, and so forth.

394.23 In Accessible Attics

Conductors in unfinished attics and roof spaces shall comply with 394.23(A) or (B).

Informational Note: See 310.14(A)(3) for temperature limitation of conductors.

(A) Accessible by Stairway or Permanent Ladder

Conductors shall be installed along the side of or through bored holes in floor joists, studs, or rafters. Where run through bored holes, conductors in the joists and in studs or rafters to a height of not less than 2.1 m (7 ft) above the floor or floor joists shall be protected by substantial running boards extending not less than 25 mm (1 in.) on each side of the conductors. Running boards shall be securely fastened in place. Running boards and guard strips shall not be required where conductors are installed along the sides of joists, studs, or rafters.

(B) Not Accessible by Stairway or Permanent Ladder

Conductors shall be installed along the sides of or through bored holes in floor joists, studs, or rafters.

Exception: In buildings completed before the wiring is installed, attic and roof spaces that are not accessible by stairway or permanent ladder and have headroom at all points less than 900 mm (3 ft), the wiring shall be permitted to be installed on the edges of rafters or joists facing the attic or roof space.

394.30 Securing and Supporting

(A) Supporting

Conductors shall be rigidly supported on noncombustible, nonabsorbent insulating materials and shall not contact any other objects. Supports shall be installed as follows:

Within 150 mm (6 in.) of each side of each tap or splice, and

At intervals not exceeding 1.4 m (41/2 ft).

Where it is impracticable to provide supports, conductors shall be permitted to be fished through hollow spaces in dry locations, provided each conductor is individually enclosed in flexible nonmetallic tubing that is in continuous lengths between supports, between boxes, or between a support and a box.

(B) Securing

Where solid knobs are used, conductors shall be securely tied thereto by tie wires having insulation equivalent to that of the conductor.

394.42 Devices

Switches shall comply with 404.4 and 404.10(B).

394.56 Splices and Taps

Splices shall be soldered unless approved splicing devices are used. In-line or strain splices shall not be used.

Part III Construction Specifications

394.104 Conductors

Conductors shall be of a type specified by Article 310.

Article 396 Messenger-Supported Wiring

Part I General

396.1 Scope

This article covers the use, installation, and construction specifications for messenger-supported wiring.

396.2 Definitions

Insulated Conductor. This definition shall apply only within this article.

For the purposes of this article, an insulated conductor includes the following:

Conductor types described in 310.4, and

Overhead service conductors encased in a polymeric material that has been evaluated for the applied nominal voltage.

Informational Note: Evidence of evaluation for the applied nominal voltage can be given by certification that the conductors have met the requirements of ICEA S-76-474-2011, Standard for Neutral Supported Power Cable Assemblies with Weather-Resistant Extruded Insulation Rated 600 Volts.

Messenger-Supported Wiring. This definition shall apply within this article and throughout the Code.

An exposed wiring support system using a messenger wire to support insulated conductors by any one of the following:

A messenger with rings and saddles for conductor support

A messenger with a field-installed lashing material for conductor support

Factory-assembled aerial cable

Multiplex cables utilizing a bare conductor, factory assembled and twisted with one or more insulated conductors, such as duplex, triplex, or quadruplex type of construction

Part II Installation

396.10 Uses Permitted

(A) Cable Types

The cable types in Table 396.10(A) shall be permitted to be installed in messenger-supported wiring under the conditions described in the article or section referenced for each.

Table 396.10(A) Cable Types

Cable Type Section Article

Medium-voltage cable 328

Metal-clad cable 330

Mineral-insulated, metal-sheathed cable 332

Multiconductor service-entrance cable 338

Multiconductor underground feeder and branch-circuit cable 340

Other factory-assembled, multiconductor control, signal, or power cables that are identified for the use

Power and control tray cable 336

Power-limited tray cable Table 725.154, 725.135(J), and 725.179(E)

(B) In Industrial Establishments

In industrial establishments only, where conditions of maintenance and supervision ensure that only qualified persons service the installed messenger-supported wiring, the following shall be permitted:

Any of the conductor types shown in Table 310.4(A) or Table 310.4(B)

MV cable

Where exposed to weather, conductors shall be listed for use in wet locations. Where exposed to direct rays of the sun, conductors or cables shall be sunlight resistant.

(C) Hazardous (Classified) Locations

Messenger-supported wiring shall be permitted to be used in hazardous (classified) locations where the contained cables and messenger-supported wiring are specifically permitted by other articles in this Code.

396.12 Uses Not Permitted

Messenger-supported wiring shall not be used in hoistways or where subject to physical damage.

396.30 Messenger

(A) Support

The messenger shall be supported at dead ends and at intermediate locations so as to eliminate tension on the conductors. The conductors shall not be permitted to come into contact with the messenger supports or any structural members, walls, or pipes.

(B) Neutral Conductor

Where the messenger is used as a neutral conductor, it shall comply with the requirements of 225.4, 250.184(A), 250.184(B)(7), and 250.187(B).

(C) Equipment Grounding Conductor

Where the messenger is used as an equipment grounding conductor, it shall comply with the requirements of 250.32(B), 250.118, 250.184(B)(8), and 250.187(D).

396.56 Conductor Splices and Taps

Conductor splices and taps made and insulated by approved methods shall be permitted in messenger-supported wiring.

396.60 Grounding

The messenger shall be grounded as required by 250.80 and 250.86 for enclosure grounding.

Article 398 Open Wiring on Insulators

Part I General

398.1 Scope

This article covers the use, installation, and construction specifications of open wiring on insulators.

398.2 Definition

The definition in this section shall apply within this article and throughout the Code.

Open Wiring on Insulators. An exposed wiring method using cleats, knobs, tubes, and flexible tubing for the protection and support of single insulated conductors run in or on buildings.

Part II Installation

398.10 Uses Permitted

Open wiring on insulators shall be permitted only for industrial or agricultural establishments on systems of 1000 volts, nominal, or less, as follows:

Indoors or outdoors

In wet or dry locations

Where subject to corrosive vapors

For services

398.12 Uses Not Permitted

Open wiring on insulators shall not be installed where concealed by the building structure.

398.15 Exposed Work

(A) Dry Locations

In dry locations, where not exposed to physical damage, conductors shall be permitted to be separately enclosed in flexible nonmetallic tubing. The tubing shall be in continuous lengths not exceeding 4.5 m (15 ft) and secured to the surface by straps at intervals not exceeding 1.4 m (41/2 ft).

(B) Entering Spaces Subject to Dampness, Wetness, or Corrosive Vapors

Conductors entering or leaving locations subject to dampness, wetness, or corrosive vapors shall have drip loops formed on them and shall then pass upward and inward from the outside of the buildings, or from the damp, wet, or corrosive location, through noncombustible, nonabsorbent insulating tubes.

Informational Note: See 230.52 for individual conductors entering buildings or other structures.

(C) Exposed to Physical Damage

Conductors within 2.1 m (7 ft) from the floor shall be considered exposed to physical damage. Where open conductors cross ceiling joists and wall studs and are exposed to physical damage, they shall be protected by one of the following methods:

Guard strips not less than 25 mm (1 in.) nominal in thickness and at least as high as the insulating supports, placed on each side of and close to the wiring.

A substantial running board at least 13 mm (1/2 in.) thick in back of the conductors with side protections. Running boards shall extend at least 25 mm (1 in.) outside the conductors, but not more than 50 mm (2 in.), and the protecting sides shall be at least 50 mm (2 in.) high and at least 25 mm (1 in.), nominal, in thickness.

Boxing made in accordance with 398.15(C)(1) or (C)(2) and furnished with a cover kept at least 25 mm (1 in.) away from the conductors within. Where protecting vertical conductors on side walls, the boxing shall be closed at the top and the holes through which the conductors pass shall be bushed.

Rigid metal conduit, intermediate metal conduit, rigid nonmetallic conduit, or electrical metallic tubing. When installed in metal piping, the conductors shall be encased in continuous lengths of approved flexible tubing.

398.17 Through or Parallel to Framing Members

Open conductors shall be separated from contact with walls, floors, wood cross members, or partitions through which they pass by tubes or bushings of noncombustible, nonabsorbent insulating material. Where the bushing is shorter than the hole, a waterproof sleeve of noninductive material shall be inserted in the hole and an insulating bushing slipped into the sleeve at each end in such a manner as to keep the conductors absolutely out of contact with the sleeve. Each conductor shall be carried through a separate tube or sleeve.

Informational Note: See 310.14(A)(3) for temperature limitation of conductors.

398.19 Clearances

Open conductors shall be separated at least 50 mm (2 in.) from metal raceways, piping, or other conducting material, and from any exposed lighting, power, or signaling conductor, or shall be separated therefrom by a continuous and firmly fixed nonconductor in addition to the insulation of the conductor. Where any insulating tube is used, it shall be secured at the ends. Where practicable, conductors shall pass over rather than under any piping subject to leakage or accumulations of moisture.

398.23 In Accessible Attics

Diagram

Conductors in unfinished attics and roof spaces shall comply with 398.23(A) or (B).

Upcodes Diagrams

(A) Accessible by Stairway or Permanent Ladder

Conductors shall be installed along the side of or through bored holes in floor joists, studs, or rafters. Where run through bored holes, conductors in the joists and in studs or rafters to a height of not less than 2.1 m (7 ft) above the floor or floor joists shall be protected by substantial running boards extending not less than 25 mm (1 in.) on each side of the conductors. Running boards shall be securely fastened in place. Running boards and guard strips shall not be required for conductors installed along the sides of joists, studs, or rafters.

(B) Not Accessible by Stairway or Permanent Ladder

Conductors shall be installed along the sides of or through bored holes in floor joists, studs, or rafters.

Exception: In buildings completed before the wiring is installed, in attic and roof spaces that are not accessible by stairway or permanent ladder and have headroom at all points less than 900 mm (3 ft), the wiring shall be permitted to be installed on the edges of rafters or joists facing the attic or roof space.

398.30 Securing and Supporting

(A) Conductor Sizes Smaller Than 8 AWG

Conductors smaller than 8 AWG shall be rigidly supported on noncombustible, nonabsorbent insulating materials and shall not contact any other objects. Supports shall be installed as follows:

Within 150 mm (6 in.) from a tap or splice

Within 300 mm (12 in.) of a dead-end connection to a lampholder or receptacle

At intervals not exceeding 1.4 m (41/2 ft) and at closer intervals sufficient to provide adequate support where likely to be disturbed

(B) Conductor Sizes 8 AWG and Larger

Supports for conductors 8 AWG or larger installed across open spaces shall be permitted up to 4.5 m (15 ft) apart if noncombustible, nonabsorbent insulating spacers are used at least every 1.4 m (41/2 ft) to maintain at least 65 mm (21/2 in.) between conductors.

Where not likely to be disturbed in buildings of mill construction, 8 AWG and larger conductors shall be permitted to be run across open spaces if supported from each wood cross member on approved insulators maintaining 150 mm (6 in.) between conductors.

(C) Industrial Establishments

In industrial establishments only, where conditions of maintenance and supervision ensure that only qualified persons service the system, conductors of sizes 250 kcmil and larger shall be permitted to be run across open spaces where supported at intervals up to 9.0 m (30 ft) apart.

(D) Mounting of Conductor Supports

Where nails are used to mount knobs, they shall not be smaller than tenpenny. Where screws are used to mount knobs, or where nails or screws are used to mount cleats, they shall be of a length sufficient to penetrate the wood to a depth equal to at least one-half the height of the knob and the full thickness of the cleat. Cushion washers shall be used with nails.

(E) Tie Wires

Conductors 8 AWG or larger and supported on solid knobs shall be securely tied thereto by tie wires having an insulation equivalent to that of the conductor.

398.42 Devices

Surface-type snap switches shall be mounted in accordance with 404.10(A), and boxes shall not be required. Other type switches shall be installed in accordance with 404.4.

Part III Construction Specifications

398.104 Conductors

Conductors shall be of a type specified by Article 310.

Article 399 Outdoor Overhead Conductors Over 1000 Volts

399.1 Scope

This article covers the use and installation for outdoor overhead conductors over 1000 volts, nominal.

399.2 Definition

The definitions in this section shall apply only within this article.

Outdoor Overhead Conductors. Single conductors, insulated, covered, or bare, installed outdoors on support structures in free air.

399.10 Uses Permitted

Outdoor overhead conductors over 1000 volts, nominal, shall be permitted only for systems rated over 1000 volts, nominal, as follows:

Outdoors in free air

For service conductors, feeders, or branch circuits

Informational Note: For additional information on outdoor overhead conductors over 1000 volts, see IEEE C2, National Electrical Safety Code, and ANSI/IEEE 3001.2, Recommended Practice for Evaluating the Electrical Service Requirements of Industrial and Commercial Power Systems.

399.30 Support

(A) Conductors

Documentation of the engineered design by a licensed professional engineer engaged primarily in the design of such systems for the spacing between conductors shall be available upon request of the authority having jurisdiction and shall include consideration of the following:

Applied voltage

Conductor size

Distance between support structures

Type of structure

Wind/ice loading

Surge protection

(B) Structures

Structures of wood, metal, or concrete, or combinations of those materials, shall be provided for support of overhead conductors over 1000 volts, nominal. Documentation of the engineered design by a licensed professional engineer engaged primarily in the design of such systems and the installation of each support structure shall be available upon request of the authority having jurisdiction and shall include consideration of the following:

Soil conditions

Foundations and structure settings

Weight of all supported conductors and equipment

Weather loading and other conditions such as, but not limited to, ice, wind, temperature, and lightning

Angle where change of direction occurs

Spans between adjacent structures

Effect of dead-end structures

Strength of guy wires and guy anchors

Structure size and material(s)

(C) Insulators

Insulators used to support conductors shall be rated for all of the following:

Applied phase-to-phase voltage

Mechanical strength required for each individual installation

Impulse withstand BIL in accordance with Table 490.24

Informational Note: 399.30(A), (B), and (C) are not all-inclusive lists.