**Chapter 40 Industrial Occupancies**

40.1 General Requirements

40.1.1 Application

40.1.1.1

The requirements of this chapter shall apply to both new and existing industrial occupancies.

40.1.1.2 Administration

The provisions of Chapter 1, Administration, shall apply.

40.1.1.3 General

The provisions of Chapter 4, General, shall apply.

40.1.1.4

Industrial occupancies shall include factories making products of all kinds and properties used for operations such as processing, assembling, mixing, packaging, finishing or decorating, repairing, and similar operations.

40.1.1.5

Incidental high hazard operations protected in accordance with Section 8.7 and 40.3.2 in occupancies containing low or ordinary hazard contents shall not be the basis for high hazard industrial occupancy classification.

40.1.2 Classification of Occupancy

Classification of occupancy shall be in accordance with 6.1.12.

40.1.2.1 Subclassification of Occupancy

Each industrial occupancy shall be subclassified according to its use as described in 40.1.2.1.1, 40.1.2.1.2, and 40.1.2.1.3.

40.1.2.1.1 General Industrial Occupancy

General industrial occupancies shall include all of the following:

Industrial occupancies that conduct ordinary and low hazard industrial operations in buildings of conventional design that are usable for various types of industrial processes

Industrial occupancies that include multistory buildings where floors are occupied by different tenants, or buildings that are usable for such occupancy and, therefore, are subject to possible use for types of industrial processes with a high density of employee population

40.1.2.1.2 Special-Purpose Industrial Occupancy

Special-purpose industrial occupancies shall include all of the following:

Industrial occupancies that conduct ordinary and low hazard industrial operations in buildings designed for, and that are usable only for, particular types of operations

Industrial occupancies that are characterized by a relatively low density of employee population, with much of the area occupied by machinery or equipment

40.1.2.1.3\* High Hazard Industrial Occupancy

High hazard industrial occupancies shall include all of the following:

Industrial occupancies that conduct industrial operations that use high hazard materials or processes or house high hazard contents

Industrial occupancies in which incidental high hazard operations in low or ordinary hazard occupancies that are protected in accordance with Section 8.7 and 40.3.2 are not required to be the basis for overall occupancy classification

40.1.2.2 Change of Industrial Occupancy Subclassification

A change from one subclassification of industrial occupancy to another shall comply with Chapter 43.

40.1.3 Multiple Occupancies

All multiple occupancies shall be in accordance with 6.1.14.

40.1.4 Definitions

40.1.4.1 General

For definitions, see Chapter 3, Definitions.

40.1.4.2 Special Definitions

Special terms applicable to this chapter are defined in Chapter 3.

40.1.5 Classification of Hazard of Contents

Classification of hazard of contents shall be in accordance with Section 6.2.

40.1.6 Minimum Construction Requirements

(No requirements.)

40.1.7\* Occupant Load

The occupant load, in number of persons for whom means of egress and other provisions are required, shall be determined on the basis of the occupant load factors of Table 7.3.1.2 that are characteristic of the use of the space, or shall be determined as the maximum probable population of the space under consideration, whichever is greater.

40.2 Means of Egress Requirements

40.2.1 General

40.2.1.1

Each required means of egress shall be in accordance with the applicable portions of Chapter 7.

40.2.1.2\*

Normally unoccupied utility chases that are secured from unauthorized access and are used exclusively for routing of electrical, mechanical, or plumbing equipment shall not be required to comply with the provisions of Chapter 7

40.2.2 Means of Egress Components

40.2.2.1 Components Permitted

Components of means of egress shall be limited to the types described in 40.2.2.2 through 40.2.2.13.

40.2.2.2 Doors

40.2.2.2.1

Doors complying with 7.2.1 shall be permitted.

40.2.2.2.2

Delayed-egress locks complying with 7.2.1.6.1 shall be permitted.

40.2.2.2.3

Access-controlled egress doors complying with 7.2.1.6.2 shall be permitted.

40.2.2.2.4

Approved existing horizontal-sliding fire doors shall be permitted in the means of egress where they comply with all of the following conditions:

They are held open by fusible links.

The fusible links are rated at not less than 165°F (74°C).

The fusible links are located not more than 10 ft (3050 mm) above the floor.

The fusible links are in immediate proximity to the door opening.

The fusible links are not located above a ceiling.

The door is not credited with providing any protection under this Code.

40.2.2.3 Stairs

40.2.2.3.1

Stairs shall comply with 7.2.2 and shall be permitted to be modified by any of the following:

Noncombustible grated stair treads and noncombustible grated landing floors shall be permitted.

Industrial equipment access stairs in accordance with 40.2.5.2 shall be permitted.

40.2.2.3.2

Spiral stairs complying with 7.2.2.2.3 shall be permitted.

40.2.2.3.3

Existing winders complying with 7.2.2.2.4 shall be permitted.

40.2.2.4 Smokeproof Enclosures

Smokeproof enclosures complying with 7.2.3 shall be permitted.

40.2.2.5 Horizontal Exits

40.2.2.5.1

Horizontal exits complying with 7.2.4 shall be permitted.

40.2.2.5.2\*

In horizontal exits where the opening is protected by a fire door assembly on each side of the wall in which it is located, one fire door shall be of the swinging type, as provided in 7.2.4.3.7, and the other shall be permitted to be an automatic-sliding fire door that shall be kept open whenever the building is occupied.

40.2.2.6 Ramps

Ramps shall comply with 7.2.5, except that industrial equipment access ramps shall be permitted to be in accordance with 40.2.5.2.

40.2.2.7 Exit Passageways

Exit passageways complying with 7.2.6 shall be permitted.

40.2.2.8 Escalators and Moving Walks

Existing previously approved escalators and moving walks complying with 7.2.7 and located within the required means of egress shall be permitted.

40.2.2.9 Fire Escape Stairs

Existing fire escape stairs complying with 7.2.8 shall be permitted.

40.2.2.10 Fire Escape Ladders

40.2.2.10.1

Fire escape ladders complying with 7.2.9 shall be permitted.

40.2.2.10.2

Fixed industrial stairs in accordance with the minimum requirements for fixed stairs in ANSI A1264.1, Safety Requirements for Workplace Floor and Wall Openings, Stairs and Railing Systems, shall be permitted where fire escape ladders are permitted in accordance with 7.2.9.1.

40.2.2.11 Slide Escapes

40.2.2.11.1

Approved slide escapes complying with 7.2.10 shall be permitted as components in 100 percent of the required means of egress for both new and existing high hazard industrial occupancies.

40.2.2.11.2

Slide escapes permitted by 40.2.2.11.1 shall be counted as means of egress only where regularly used in emergency egress drills to ensure that occupants are familiar with their use through practice.

40.2.2.12 Alternating Tread Devices

Alternating tread devices complying with 7.2.11 shall be permitted.

40.2.2.13 Areas of Refuge

Areas of refuge complying with 7.2.12 shall be permitted.

40.2.3 Capacity of Means of Egress

Capacity of means of egress shall comply with either 40.2.3.1 or 40.2.3.2.

40.2.3.1

The capacity of means of egress shall be in accordance with Section 7.3.

40.2.3.2

In industrial occupancies, means of egress shall be sized to accommodate the occupant load as determined in accordance with 40.1.7; spaces not subject to human occupancy because of the presence of machinery or equipment shall not be included in the computation.

40.2.4 Number of Means of Egress

See also Section 7.4.

40.2.4.1

The number of means of egress shall comply with either 40.2.4.1.1 or 40.2.4.1.2.

40.2.4.1.1

Not less than two means of egress shall be provided from every story or section, and not less than one exit shall be reached without traversing another story.

40.2.4.1.2

A single means of egress shall be permitted from any story or section in low and ordinary hazard industrial occupancies, provided that the exit can be reached within the distance permitted as a common path of travel.

40.2.4.2

In new buildings, floors or portions thereof with an occupant load of more than 500 shall have the minimum number of separate and remote means of egress specified by 7.4.1.2.

40.2.4.3

Areas with high hazard contents shall comply with Section 7.11.

40.2.5 Arrangement of Means of Egress

Means of egress, arranged in accordance with Section 7.5, shall not exceed that provided by Table 40.2.5.

Table 40.2.5 Arrangement of Means of Egress

Level of Protection General Industrial Occupancy Special-Purpose Industrial Occupancy High Hazard Industrial Occupancy

ft m ft m

Dead-End Corridor

Protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1) 50 15 50 15 Prohibited, except as permitted by 7.11.4

Not protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1) 50 15 50 15 Prohibited, except as permitted by 7.11.4

Common Path of Travel

Protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1) 100 30 100 30 Prohibited, except as permitted by 7.11.4

Not protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1) 50 15 50 15 Prohibited, except as permitted by 7.11.4

40.2.5.1 Ancillary Facilities

40.2.5.1.1\*

New ancillary facilities shall be arranged to allow travel in independent directions after leaving the ancillary facility so that both means of egress paths do not become compromised by the same fire or similar emergency.

40.2.5.1.2\*

New ancillary facilities in special-purpose industrial occupancies where delayed evacuation is anticipated shall have not less than a 2-hour fire resistance—rated separation from the predominant industrial occupancy, and shall have one means of egress that is separated from the predominant industrial occupancy by 2-hour fire resistance—rated construction.

40.2.5.2 Industrial Equipment Access

40.2.5.2.1

Industrial equipment access doors, walkways, platforms, ramps, and stairs that serve as a component of the means of egress from the involved equipment shall be permitted in accordance with the applicable provisions of Chapter 7, as modified by Table 40.2.5.2.1.

Table 40.2.5.2.1 Industrial Equipment Access Dimensional Criteria

Feature Dimensional Criteria

Minimum horizontal dimension of any walkway, landing, or platform 22 in. (560 mm) clear

Minimum stair or ramp width 22 in. (560 mm) clear between rails

Minimum tread width 22 in. (560 mm) clear

Minimum tread depth 10 in. (255 mm)

Maximum riser height 9 in. (230 mm)

Handrails are permitted to terminate, at the required height, at a point directly above the top and bottom risers.

Maximum height between landings 12 ft (3660 mm)

Minimum headroom 6 ft 8 in. (2030 mm)

Minimum width of door openings 22 in. (560 mm) clear

40.2.5.2.2

Any means of egress component permitted by 40.2.5.2.1 shall serve not more than 20 people.

40.2.6 Travel Distance to Exits

Travel distance, measured in accordance with Section 7.6, shall not exceed that provided by Table 40.2.6.

Table 40.2.6 Maximum Travel Distance to Exits

Level of Protection General Industrial Occupancy Special-Purpose Industrial Occupancy High Hazard Industrial Occupancy

ft m ft m ft m

Protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1) 250† 76† 400 122 75 23

Not protected throughout by an approved, supervised automatic sprinkler system in accordance with 9.7.1.1(1) 200 61 300 91 NP NP

NP: Not permitted.

†In one-story buildings, a travel distance of 400 ft (122 m) is permitted, provided that a performance-based analysis demonstrates that safe egress can be accomplished.

40.2.7 Discharge From Exits

Discharge from exits shall be in accordance with Section 7.7.

40.2.8 Illumination of Means of Egress

Means of egress shall be illuminated in accordance with Section 7.8 or with natural lighting that provides the required level of illumination in structures occupied only during daylight hours.

40.2.9\* Emergency Lighting

40.2.9.1

Emergency lighting shall be provided in accordance with Section 7.9, except as otherwise exempted by 40.2.9.2.

40.2.9.2

Emergency lighting shall not be required for any of the following:

Special-purpose industrial occupancies without routine human habitation

Structures occupied only during daylight hours, with skylights or windows arranged to provide the required level of illumination on all portions of the means of egress during such hours

40.2.10 Marking of Means of Egress

Means of egress shall have signs in accordance with Section 7.10.

40.2.11 Special Means of Egress Features

40.2.11.1 Reserved

40.2.11.2 Lockups

40.2.11.2.1

Lockups in new industrial occupancies shall comply with the requirements of 22.4.5.

40.2.11.2.2

Lockups in existing industrial occupancies, other than approved existing lockups, shall comply with the requirements of 23.4.5.

40.3 Protection

40.3.1 Protection of Vertical Openings

Any vertical opening shall be protected in accordance with Section 8.6, unless otherwise permitted by one of the following:

In special-purpose industrial and high hazard industrial occupancies where unprotected vertical openings exist and are necessary to manufacturing operations, such openings shall be permitted beyond the specified limits, provided that every floor level has direct access to one or more enclosed stairs or other exits protected against obstruction by any fire or smoke in the open areas connected by the unprotected vertical openings.

Approved existing open stairs, existing open ramps, and existing escalators shall be permitted where connecting only two floor levels.

Approved, existing, unprotected vertical openings in buildings with low or ordinary hazard contents that are protected throughout by an approved automatic sprinkler system in accordance with 9.7.1.1(1) shall be permitted, provided that the following conditions exist:

The vertical opening does not serve as a required exit.

All required exits consist of outside stairs in accordance with 7.2.2, smokeproof enclosures in accordance with 7.2.3, or horizontal exits in accordance with 7.2.4.

Vertical openings in accordance with 8.6.9.1 shall be permitted.

40.3.2\* Protection From Hazards

40.3.2.1

All high hazard industrial occupancies, operations, or processes shall have approved, supervised automatic extinguishing systems in accordance with Section 9.7 or other protection appropriate to the particular hazard, such as explosion venting or suppression.

40.3.2.2

Protection in accordance with 40.3.2.1 shall be provided for any area subject to an explosion hazard in order to minimize danger to occupants in case of fire or other emergency before they have time to use exits to escape.

40.3.2.3

Activation of the fire-extinguishing or suppression system required by 40.3.2.1 shall initiate the required building fire alarm system in accordance with 40.3.4.3.4.

40.3.2.4

Hazardous areas in industrial occupancies protected by approved automatic extinguishing systems in accordance with Section 9.7 shall be exempt from the smoke-resisting enclosure requirement of 8.7.1.2.

40.3.3 Interior Finish

40.3.3.1 General

Interior finish shall be in accordance with Section 10.2.

40.3.3.2 Interior Wall and Ceiling Finish

Interior wall and ceiling finish materials complying with Section 10.2 shall be Class A, Class B, or Class C in operating areas and shall be as required by 7.1.4 in exit enclosures.

40.3.3.3 Interior Floor Finish

40.3.3.3.1

Interior floor finish in exit enclosures and in exit access corridors shall be not less than Class II.

40.3.3.3.2

Interior floor finish in areas other than those specified in 40.3.3.3.1 shall not be required to comply with Section 10.2.

40.3.4 Detection, Alarm, and Communications Systems

40.3.4.1 General

A fire alarm system shall be required in accordance with Section 9.6 for industrial occupancies, unless the total occupant load of the building is under 100 persons and unless, of these, fewer than 25 persons are above or below the level of exit discharge.

40.3.4.2 Initiation

Initiation of the required fire alarm system shall be by any of the following means:

Manual means in accordance with 9.6.2.1(1)

Approved automatic fire detection system in accordance with 9.6.2.1(2) throughout the building, plus a minimum of one manual fire alarm box in accordance with 9.6.2.6

Approved, supervised automatic sprinkler system in accordance with 9.6.2.1(3) throughout the building, plus a minimum of one manual fire alarm box in accordance with 9.6.2.6

40.3.4.3 Notification

40.3.4.3.1

The required fire alarm system shall meet one of the following criteria:

It shall provide occupant notification in accordance with 9.6.3.

It shall sound an audible and visible signal in a constantly attended location for the purposes of initiating emergency action.

40.3.4.3.2

Positive alarm sequence in accordance with 9.6.3.4 shall be permitted.

40.3.4.3.3

Existing presignal systems in accordance with 9.6.3.3 shall be permitted.

40.3.4.3.4

In high hazard industrial occupancies, as described in 40.1.2.1.3, the required fire alarm system shall automatically initiate an occupant evacuation alarm signal in accordance with 9.6.3.

40.3.5 Extinguishment Requirements

(No requirements.)

40.3.6 Corridors

The provisions of 7.1.3.1 shall not apply.

40.4 Special Provisions — High-Rise Buildings

New high-rise industrial occupancies shall comply with Section 11.8.

40.4.1

The provisions of 11.8.5.2.4(2) for jockey pumps and 11.8.5.2.4(3) for air compressors serving dry-pipe and pre-action systems shall not apply to special-purpose industrial occupancies.

40.5 Building Services

40.5.1 Utilities

Utilities shall comply with the provisions of Section 9.1.

40.5.2 Heating, Ventilating, and Air-Conditioning

Heating, ventilating, and air-conditioning equipment shall comply with the provisions of Section 9.2.

40.5.3 Elevators, Escalators, and Conveyors

Elevators, escalators, and conveyors shall comply with the provisions of Section 9.4.

40.5.4 Rubbish Chutes, Incinerators, and Laundry Chutes

Rubbish chutes, incinerators, and laundry chutes shall comply with the provisions of Section 9.5.

40.6\* Special Provisions for Aircraft Servicing Hangars

40.6.1

The requirements of Sections 40.1 through 40.5 shall be met, except as modified by 40.6.1.1 through 40.6.1.4.

40.6.1.1

There shall be not less than two means of egress from each aircraft servicing area.

40.6.1.2

Exits from aircraft servicing areas shall be provided at intervals not exceeding 150 ft (46 m) on all exterior walls.

40.6.1.3

Where horizontal exits are provided, doors shall be provided in the horizontal exit fire barrier at intervals not exceeding 100 ft (30 m).

40.6.1.4

Where dwarf, or "smash," doors are provided in doors that accommodate aircraft, such doors shall be permitted for compliance with 40.6.1.1 through 40.6.1.3.

40.6.2

Means of egress from mezzanine floors in aircraft servicing areas shall be arranged so that the travel distance to the nearest exit from any point on the mezzanine does not exceed 75 ft (23 m), and such means of egress shall lead directly to a properly enclosed stair discharging directly to the exterior, to a suitable cutoff area, or to outside stairs.

40.6.3

Dead ends shall not exceed 50 ft (15 m) for other than high hazard contents areas and shall not be permitted for high hazard contents areas.

40.7.1 Upholstered Furniture and Mattresses

The provisions of 10.3.2 shall not apply to upholstered furniture and mattresses.

40.7.2 Soiled Linen and Trash Receptacles

The requirements of 10.3.9 for containers for rubbish, waste, or linen with a capacity of 20 gal (75.7 L) or more shall not apply.